## NG Boiler C Small v2
| Condensing Boilers | Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
| Condensing boiler PL | 3 | 97.2% | 107.6% | [138] | 2.7884 | PL | 1_NG | 1_Heat | 2_NG | 2_Heat
| Condensing boiler NL | 14.3 | 87.8% | 97.18% | [138] | 14.7145 | NL | 1.9499 | 2.0979 | 10.2898 | 10
| Condensing boiler PL | 3.8 | 97.3% | 107.7% | [138] | 3.5284 | PL
| Condensing boiler NL | 18.7 | 88.1% | 97.52% | [138] | 19.1765 | NL
| Condensing boiler PL | 4.5 | 97.3% | 107.7% | [138] | 4.1783 | PL | 1_NG | 1_Heat | 2_NG | 2_Heat
| Condensing boiler NL | 25 | 88.2% | 97.63% | [138] | 25.6079 | NL | 3.3427 | 3.6 | 20.4864 | 20
| Condensing boiler PL | 5.2 | 97.4% | 107.8% | [138] | 4.8233 | PL | 1_NG | 1_Heat | 2_NG | 2_Heat
| Condensing boiler NL | 33 | 88.2% | 97.63% | [138] | 33.8025 | NL | 4.3849 | 4.7273 | 30.7295 | 30
| Condensing boiler PL | 7.5 | 97.4% | 107.8% | [138] | 6.9567 | PL
| Condensing boiler NL | 46 | 88.3% | 97.74% | [138] | 47.0653 | NL
| Condensing boiler PL | 12.1 | 97.4% | 107.8% | [138] | 11.2235 | PL | 1_NG | 1_Heat | 2_NG | 2_Heat
| Condensing boiler NL | 64.5 | 88.3% | 97.74% | [138] | 65.9937 | NL | 10.4405 | 11.2558 | 61.3895 | 60
| Condensing boiler PL | 18.6 | 97% | 107.4% | [139] | 17.3239 | PL
| Condensing boiler NL | 91.2 | 88.2% | 97.63% | [139] | 93.4178 | NL
| Condensing boiler PL | 19 | 97.4% | 107.8% | [138] | 17.6237 | PL
| Condensing boiler NL | 92 | 87.9% | 97.29% | [138] | 94.5589 | NL
| Condensing boiler PL | 20.7 | 95.8% | 106% | [139] | 19.5213 | PL | 1_NG | 1_Heat | 2_NG | 2_Heat
| Condensing boiler NL | 109.7 | 88.9% | 98.4% | [139] | 111.4829 | NL | 17.7951 | 18.8696 | 101.6252 | 100
| Ref | Link
[138] | Hoval UltraGas Description ® (15-100) Floor-standing gas condensing boiler | https://edergen.be/uploads/downloads/Hoval-UltraGas-15-100-EN.pdf
[139] | Hoval TopGas Description ® classic (100,120) Wall-hanging gas condensing boiler | https://cdn.hoval.com/topgas-classic-100-120-exa-en-25-hybris-original.pdf
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_HHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 14.3 | 2.7884 | 3 | 2.9045 | 3.184%
| NL | 14.3 | 14.7145 | 14.3 | 14.3306 | -0.2141%
| PL | 18.7 | 3.5284 | 3.8 | 3.7079 | 2.423%
| NL | 18.7 | 19.1765 | 18.7 | 18.7001 | -0.0005576%
| PL | 25 | 4.1783 | 4.5 | 4.4659 | 0.7569%
| NL | 25 | 25.6079 | 25 | 24.9973 | 0.01083%
| PL | 33 | 4.8233 | 5.2 | 5.2557 | -1.072%
| NL | 33 | 33.8025 | 33 | 33.0202 | -0.06114%
| PL | 46 | 6.9567 | 7.5 | 7.5789 | -1.052%
| NL | 46 | 47.0653 | 46 | 46.0062 | -0.01356%
| PL | 64.5 | 11.2235 | 12.1 | 12.0642 | 0.2956%
| NL | 64.5 | 65.9937 | 64.5 | 64.5386 | -0.05983%
| PL | 91.2 | 17.3239 | 18.6 | 18.4823 | 0.6326%
| NL | 91.2 | 93.4178 | 91.2 | 91.3866 | -0.2047%
| PL | 92 | 17.6237 | 19 | 18.7868 | 1.122%
| NL | 92 | 94.5589 | 92 | 92.4971 | -0.5403%
| PL | 109.7 | 19.5213 | 20.7 | 20.985 | -1.377%
| NL | 109.7 | 111.4829 | 109.7 | 109.0919 | 0.5544%
| k1 | k2 | k3
| 0.95808 | 0.021479 | -0.074215
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.2 | 0.2131 |  |  | 1 | 0.97956

## Check NG BOILER Small C
| Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 3 | 97.2% | 107.6% | [152][153] | 2.7884 | PL
Non Condensing boiler PL | 7.15 | 96.2% | 106.5% | [152][153] | 6.7148 | PL
Non Condensing boiler PL | 11.44 | 94.4% | 104.5% | [152][153] | 10.9486 | PL
Non Condensing boiler NL | 14.3 | 87.8% | 97.18% | [152][153] | 14.7145 | NL
| Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 7.5 | 97.4% | 107.8% | [152][153] | 6.9567 | PL
Non Condensing boiler PL | 23 | 96.4% | 106.7% | [152][153] | 21.5553 | PL
Non Condensing boiler PL | 36.8 | 94.6% | 104.7% | [152][153] | 35.1447 | PL
Non Condensing boiler NL | 46 | 88.3% | 97.74% | [152][153] | 47.0653 | NL
| Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 20.7 | 95.8% | 106% | [152][153] | 19.5213 | PL
Non Condensing boiler PL | 54.85 | 94.8% | 104.9% | [152][153] | 52.2723 | PL
Non Condensing boiler PL | 87.76 | 93.1% | 103% | [152][153] | 85.1629 | PL
Non Condensing boiler NL | 109.7 | 88.9% | 98.4% | [152][153] | 111.4829 | NL

## NG Boiler C Mid-Big
| Condensing Boilers | Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
| Condensing boiler PL | 25.7 | 97.21% | 107.6% | [154] | 23.8848 | PL
| Condensing boiler NL | 150 | 94.86% | 105% | [154] | 142.8571 | NL
| Condensing boiler PL | 37.3 | 97.75% | 108.2% | [154] | 34.4732 | PL
| Condensing boiler NL | 200 | 95.13% | 105.3% | [154] | 189.9335 | NL
| Condensing boiler PL | 42.9 | 97.93% | 108.4% | [154] | 39.5756 | PL
| Condensing boiler NL | 250 | 94.95% | 105.1% | [154] | 237.8687 | NL
| Condensing boiler PL | 51.4 | 97.57% | 108% | [154] | 47.5926 | PL
| Condensing boiler NL | 300 | 94.86% | 105% | [154] | 285.7143 | NL
| Condensing boiler PL | 120.6 | 98.4% | 108.9% | [155] | 110.7275 | PL
| Condensing boiler NL | 402 | 95% | 105.2% | [155] | 382.3013 | NL
| Condensing boiler PL | 150.3 | 98.4% | 108.9% | [155] | 137.9962 | PL | 1_NG | 1_Heat | 2_NG | 2_Heat
| Condensing boiler NL | 501 | 95.1% | 105.3% | [155] | 475.9491 | NL | 137.7208 | 150 | 474.9991 | 500
| Condensing boiler PL | 166.8 | 98.4% | 108.9% | [155] | 153.1455 | PL
| Condensing boiler NL | 556 | 95% | 105.2% | [155] | 528.755 | NL
| Condensing boiler PL | 187.5 | 98.4% | 108.9% | [155] | 172.151 | PL
| Condensing boiler NL | 625 | 95% | 105.2% | [155] | 594.3739 | NL
| Ref | Link
[154] | Bosch Condens 7000F Boiler | https://hmg-attachments.s3-eu-west-1.amazonaws.com/U91877_Datasheet.pdf?utm_source=chatgpt.com
[155] | VITOCROSSAL 200 | https://www.viessmann-us.com/content/dam/public-brands/ca/pdfs/gas-fired/vitocrossal_200-cm2_lg_gw6b_tdm.pdf/_jcr_content/renditions/original./vitocrossal_200-cm2_lg_gw6b_tdm.pdf
[188] | LHV & HHV for NG | https://www.engineeringtoolbox.com/fuels-higher-calorific-values-d_169.html
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 150 | 23.8848 | 25.7 | 25.887 | -0.7275%
| NL | 150 | 142.8571 | 150 | 149.4167 | 0.3889%
| PL | 200 | 34.4732 | 37.3 | 37.6593 | -0.9633%
| NL | 200 | 189.9335 | 200 | 199.0746 | 0.4627%
| PL | 250 | 39.5756 | 42.9 | 43.7355 | -1.948%
| NL | 250 | 237.8687 | 250 | 249.6243 | 0.1503%
| PL | 300 | 47.5926 | 51.4 | 52.8378 | -2.797%
| NL | 300 | 285.7143 | 300 | 300.0809 | -0.02698%
| PL | 402 | 110.7275 | 120.6 | 119.9789 | 0.515%
| NL | 402 | 382.3013 | 402 | 401.9555 | 0.01107%
| PL | 501 | 137.9962 | 150.3 | 149.8332 | 0.3106%
| NL | 501 | 475.9491 | 501 | 500.7316 | 0.05358%
| PL | 556 | 153.1455 | 166.8 | 166.4189 | 0.2285%
| NL | 556 | 528.755 | 556 | 556.4164 | -0.07489%
| PL | 625 | 172.151 | 187.5 | 187.2265 | 0.1459%
| NL | 625 | 594.3739 | 625 | 625.6229 | -0.09966%
| k1 | k2 | k3
| 1.0383 | 0.015566 | -1.2476
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.2 | 0.22323 |  |  | 1 | 1.0539

## Check NG BOILER Mid-Big C
| Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 45 | 97.2% | 107.6% | [152][153] | 41.8263 | PL
Non Condensing boiler PL | 75 | 96.2% | 106.5% | [152][153] | 70.4352 | PL
Non Condensing boiler PL | 120 | 94.4% | 104.5% | [152][153] | 114.8451 | PL
Non Condensing boiler NL | 150 | 94.9% | 105% | [152][153] | 142.8 | NL
| Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 120.6 | 98.4% | 108.9% | [152][153] | 110.7275 | PL
Non Condensing boiler PL | 201 | 97.4% | 107.8% | [152][153] | 186.4406 | PL
Non Condensing boiler PL | 321.6 | 95.6% | 105.8% | [152][153] | 303.9215 | PL
Non Condensing boiler NL | 402 | 95% | 105.2% | [152][153] | 382.3013 | NL
| Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 187.5 | 98.4% | 108.9% | [152][153] | 172.151 | PL
Non Condensing boiler PL | 312.5 | 97.4% | 107.8% | [152][153] | 289.8641 | PL
Non Condensing boiler PL | 500 | 95.6% | 105.8% | [152][153] | 472.5148 | PL
Non Condensing boiler NL | 625 | 95% | 105.2% | [152][153] | 594.3739 | NL

## NG Boiler NC
| Non Condensing Boilers | Size [BHP] | Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
| Non Condensing boiler PL | 25 | 245.2675 | 84.4% | 93.42% | [152][153] | 262.5432 | PL |  |  |  |  | 1_El e 2_El per altri
| Non Condensing boiler NL | 100 | 981.07 | 84.4% | 93.42% | [152][153] | 1050.173 | NL
| Non Condensing boiler PL | 31.25 | 306.5844 | 83.3% | 92.2% | [152][153] | 332.5128 | PL
| Non Condensing boiler NL | 125 | 1226.3375 | 83.2% | 92.09% | [152][153] | 1331.6496 | NL
| Non Condensing boiler PL | 37.5 | 367.9013 | 84.4% | 93.42% | [152][153] | 393.8149 | PL
| Non Condensing boiler NL | 150 | 1471.605 | 84.3% | 93.31% | [152][153] | 1577.1281 | NL
| Non Condensing boiler PL | 50 | 490.535 | 85% | 94.08% | [152][153] | 521.38 | PL
| Non Condensing boiler NL | 200 | 1962.14 | 84.9% | 93.97% | [152][153] | 2087.9764 | NL
| Non Condensing boiler PL | 62.5 | 613.1688 | 85% | 94.08% | [152][153] | 651.725 | PL
| Non Condensing boiler NL | 250 | 2452.675 | 83.3% | 92.2% | [152][153] | 2660.102 | NL
| Non Condensing boiler PL | 75 | 735.8025 | 85.3% | 94.42% | [152][153] | 779.3195 | PL
| Non Condensing boiler NL | 300 | 2943.21 | 83.9% | 92.87% | [152][153] | 3169.2944 | NL
| Non Condensing boiler PL | 87.5 | 858.4363 | 85.3% | 94.42% | [152][153] | 909.206 | PL
| Non Condensing boiler NL | 350 | 3433.745 | 84.5% | 93.53% | [152][153] | 3671.2556 | NL
| Non Condensing boiler PL | 100 | 981.07 | 84.5% | 93.53% | [152][153] | 1048.9302 | PL
| Non Condensing boiler NL | 400 | 3924.28 | 84.4% | 93.42% | [152][153] | 4200.6919 | NL
| Non Condensing boiler PL | 125 | 1226.3375 | 85.5% | 94.64% | [152][153] | 1295.8275 | PL
| Non Condensing boiler NL | 500 | 4905.35 | 85.2% | 94.31% | [152][153] | 5201.561 | NL
| Non Condensing boiler PL | 150 | 1471.605 | 85.7% | 94.86% | [152][153] | 1551.3641 | PL
| Non Condensing boiler NL | 600 | 5886.42 | 85.6% | 94.75% | [152][153] | 6212.7056 | NL
| Non Condensing boiler PL | 175 | 1716.8725 | 85.7% | 94.86% | [152][153] | 1809.9247 | PL
| Non Condensing boiler NL | 700 | 6867.49 | 85.7% | 94.86% | [152][153] | 7239.6989 | NL
| Non Condensing boiler PL | 200 | 1962.14 | 85.8% | 94.97% | [152][153] | 2066.0746 | PL | 1_NG | 1_Heat | 2_NG | 2_Heat
| Non Condensing boiler NL | 800 | 7848.56 | 85.6% | 94.75% | [152][153] | 8283.6075 | NL | 7897.2751 | 7500 | 31662.9069 | 30000
| Ref | Link
[152] | CBLE Firetube Boiler | https://it.scribd.com/document/80458550/CB-7768-Gen-boiler-Efficiency-Tables |  |  |  | accessed 2/11/2025
[153] | CBLE Firetube Boiler | https://cleaverbrooks.com/Catalog/boilers/firetube/cble
[188] | LHV & HHV for NG | https://www.engineeringtoolbox.com/fuels-higher-calorific-values-d_169.html
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 981.07 | 262.5432 | 245.2675 | 226.205 | 7.772%
| NL | 981.07 | 1050.173 | 981.07 | 968.5585 | 1.275%
| PL | 1226.3375 | 332.5128 | 306.5844 | 293.8007 | 4.17%
| NL | 1226.3375 | 1331.6496 | 1226.3375 | 1235.503 | -0.7474%
| PL | 1471.605 | 393.8149 | 367.9013 | 353.2272 | 3.989%
| NL | 1471.605 | 1577.1281 | 1471.605 | 1468.5186 | 0.2097%
| PL | 1962.14 | 521.38 | 490.535 | 476.756 | 2.809%
| NL | 1962.14 | 2087.9764 | 1962.14 | 1953.2979 | 0.4506%
| PL | 2452.675 | 651.725 | 613.1688 | 602.9049 | 1.674%
| NL | 2452.675 | 2660.102 | 2452.675 | 2495.832 | -1.76%
| PL | 2943.21 | 779.3195 | 735.8025 | 726.4613 | 1.27%
| NL | 2943.21 | 3169.2944 | 2943.21 | 2979.0504 | -1.218%
| PL | 3433.745 | 909.206 | 858.4363 | 852.1781 | 0.729%
| NL | 3433.745 | 3671.2556 | 3433.745 | 3455.4535 | -0.6322%
| PL | 3924.28 | 1048.9302 | 981.07 | 987.1669 | -0.6215%
| NL | 3924.28 | 4200.6919 | 3924.28 | 3957.7522 | -0.853%
| PL | 4905.35 | 1295.8275 | 1226.3375 | 1226.4648 | -0.01038%
| NL | 4905.35 | 5201.561 | 4905.35 | 4907.6804 | -0.04751%
| PL | 5886.42 | 1551.3641 | 1471.605 | 1473.9054 | -0.1563%
| NL | 5886.42 | 6212.7056 | 5886.42 | 5867.2934 | 0.3249%
| PL | 6867.49 | 1809.9247 | 1716.8725 | 1724.1962 | -0.4266%
| NL | 6867.49 | 7239.6989 | 6867.49 | 6841.8442 | 0.3734%
| PL | 7848.56 | 2066.0746 | 1962.14 | 1972.2147 | -0.5135%
| NL | 7848.56 | 8283.6075 | 7848.56 | 7832.3377 | 0.2067%
| k1 | k2 | k3
| 0.94252 | 0.0067205 | -27.8394
| L_min | 25%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.25 | 0.24235 |  |  | 1 | 0.94924
[5 empty] | HEAT | HEAT
| Non Condensing Boilers | Size [kw_th] | eff [%] LHV | input [kW_LHV] | Out calc (output) [kW_th] | Out err
Non Condensing boiler | PL | 245.2675 | 93.42% | 262.5432 | 226.205 | 7.772%
| NL | 981.07 | 93.42% | 1050.173 | 968.5585 | 1.275%
Non Condensing boiler | PL | 306.5844 | 92.2% | 332.5128 | 293.8007 | 4.17%
| NL | 1226.3375 | 92.09% | 1331.6496 | 1235.503 | -0.7474%
Non Condensing boiler | PL | 367.9013 | 93.42% | 393.8149 | 353.2272 | 3.989%
| NL | 1471.605 | 93.31% | 1577.1281 | 1468.5186 | 0.2097%
Non Condensing boiler | PL | 490.535 | 94.08% | 521.38 | 476.756 | 2.809%
| NL | 1962.14 | 93.97% | 2087.9764 | 1953.2979 | 0.4506%
Non Condensing boiler | PL | 613.1688 | 94.08% | 651.725 | 602.9049 | 1.674%
| NL | 2452.675 | 92.2% | 2660.102 | 2495.832 | -1.76%
Non Condensing boiler | PL | 735.8025 | 94.42% | 779.3195 | 726.4613 | 1.27%
| NL | 2943.21 | 92.87% | 3169.2944 | 2979.0504 | -1.218%
Non Condensing boiler | PL | 858.4363 | 94.42% | 909.206 | 852.1781 | 0.729%
| NL | 3433.745 | 93.53% | 3671.2556 | 3455.4535 | -0.6322%
Non Condensing boiler | PL | 981.07 | 93.53% | 1048.9302 | 987.1669 | -0.6215%
| NL | 3924.28 | 93.42% | 4200.6919 | 3957.7522 | -0.853%
Non Condensing boiler | PL | 1226.3375 | 94.64% | 1295.8275 | 1226.4648 | -0.01038%
| NL | 4905.35 | 94.31% | 5201.561 | 4907.6804 | -0.04751%
Non Condensing boiler | PL | 1471.605 | 94.86% | 1551.3641 | 1473.9054 | -0.1563%
| NL | 5886.42 | 94.75% | 6212.7056 | 5867.2934 | 0.3249%
Non Condensing boiler | PL | 1716.8725 | 94.86% | 1809.9247 | 1724.1962 | -0.4266%
| NL | 6867.49 | 94.86% | 7239.6989 | 6841.8442 | 0.3734%
Non Condensing boiler | PL | 1962.14 | 94.97% | 2066.0746 | 1972.2147 | -0.5135%
| NL | 7848.56 | 94.75% | 8283.6075 | 7832.3377 | 0.2067%

## Check NG BOILER NC
| Size [BHP] | Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 25 | 245.2675 | 84.4% | 93.42% | [152][153] | 262.5432 | PL
Non Condensing boiler PL | 50 | 490.535 | 85% | 94.08% | [152][153] | 521.38 | PL
Non Condensing boiler PL | 75 | 735.8025 | 84.8% | 93.86% | [152][153] | 783.9145 | PL
Non Condensing boiler NL | 100 | 981.07 | 84.4% | 93.42% | [152][153] | 1050.173 | NL
| Size [BHP] | Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 200 | 1962.14 | 85.8% | 94.97% | [152][153] | 2066.0746 | PL
Non Condensing boiler PL | 400 | 3924.28 | 86.1% | 95.3% | [152][153] | 4117.7515 | PL
Non Condensing boiler PL | 600 | 5886.42 | 85.9% | 95.08% | [152][153] | 6191.0081 | PL
Non Condensing boiler NL | 800 | 7848.56 | 85.6% | 94.75% | [152][153] | 8283.6075 | NL
| Size [BHP] | Size [kw_th] | eff [%] HHV | eff [%] LHV | ref eff, min load | input [kW_LHV]
Non Condensing boiler PL | 100 | 981.07 | 84.5% | 93.53% | [152][153] | 1048.9302 | PL
Non Condensing boiler PL | 200 | 1962.14 | 84.7% | 93.75% | [152][153] | 2092.9067 | PL
Non Condensing boiler PL | 300 | 2943.21 | 84.6% | 93.64% | [152][153] | 3143.0709 | PL
Non Condensing boiler NL | 400 | 3924.28 | 84.4% | 93.42% | [152][153] | 4200.6919 | NL

## Small Wood Chips Boiler v2
| Wood Chip Boiler | Size [kw_th] | eff (%) | ref eff, min load | input [kW_LHV]
| Decentralized Wood Chip Boiler PL | 6 | 92.4% | [140] | 6.4935 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 20 | 94.8% | [140] | 21.097 | NL | 6.4935 | 6 | 21.097 | 20
| Decentralized Wood Chip Boiler PL | 9 | 93.5% | [140] | 9.6257 | PL
| Decentralized Wood Chip Boiler NL | 30 | 95.1% | [140] | 31.5457 | NL
| Decentralized Wood Chip Boiler PL | 9.8 | 93.8% | [140] | 10.4478 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 33 | 95.2% | [140] | 34.6639 | NL | 11.081 | 10.3939 | 36.7647 | 35
| Decentralized Wood Chip Boiler PL | 12 | 94.6% | [140] | 12.685 | PL
| Decentralized Wood Chip Boiler NL | 40 | 95.4% | [140] | 41.9287 | NL
| Decentralized Wood Chip Boiler PL | 13.5 | 94.6% | [140] | 14.2706 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 45 | 95.3% | [140] | 47.2193 | NL | 14.2706 | 13.5 | 47.2193 | 45
| Decentralized Wood Chip Boiler PL | 14.9 | 94.5% | [140] | 15.7672 | PL
| Decentralized Wood Chip Boiler NL | 50 | 95.3% | [140] | 52.4659 | NL
| Decentralized Wood Chip Boiler PL | 18 | 94.5% | [140] | 19.0476 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 60 | 95.2% | [140] | 63.0252 | NL | 19.0476 | 18 | 63.0252 | 60
| Decentralized Wood Chip Boiler PL | 19.5 | 94.4% | [140] | 20.6568 | PL
| Decentralized Wood Chip Boiler NL | 65 | 95.1% | [140] | 68.3491 | NL
| Decentralized Wood Chip Boiler PL | 20.9 | 94.4% | [140] | 22.1398 | PL
| Decentralized Wood Chip Boiler NL | 70 | 95% | [140] | 73.6842 | NL
| Decentralized Wood Chip Boiler PL | 24 | 94.3% | [140] | 25.4507 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 80 | 94.9% | [140] | 84.2993 | NL | 25.4507 | 24 | 84.2993 | 80
| Decentralized Wood Chip Boiler PL | 30 | 95% | [140] | 31.5789 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 100 | 95.3% | [140] | 104.9318 | NL | 31.2632 | 29.7 | 103.8825 | 99
| Decentralized Wood Chip Boiler PL | 32.4 | 95.2% | [140] | 34.0336 | PL
| Decentralized Wood Chip Boiler NL | 108 | 95.5% | [140] | 113.089 | NL
| Decentralized Wood Chip Boiler PL | 36 | 95.6% | [140] | 37.6569 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 120 | 95.7% | [140] | 125.3918 | NL | 37.6569 | 36 | 125.3918 | 120
| Ref | Link
[140] | Wood chip & Pellet heating systems 20 – 150 kW - Technology & Planning 2025 | https://www.kwb.net/fileadmin/media/EN/Technik_Planung_Anleitungen_PDF/KWB_T_P_EN_04_2025_Modul_E_Wood_chip_and_pellet_Heatings_system_20-150_kW.pdf
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 20 | 6.4935 | 6 | 5.995 | 0.08297%
| NL | 20 | 21.097 | 20 | 19.9461 | 0.2695%
| PL | 30 | 9.6257 | 9 | 8.996 | 0.04453%
| NL | 30 | 31.5457 | 30 | 29.9367 | 0.211%
| PL | 33 | 10.4478 | 9.8 | 9.784 | 0.1635%
| NL | 33 | 34.6639 | 33 | 32.9181 | 0.2481%
| PL | 40 | 12.685 | 12 | 11.9274 | 0.6052%
| NL | 40 | 41.9287 | 40 | 39.8645 | 0.3387%
| PL | 45 | 14.2706 | 13.5 | 13.4465 | 0.3961%
| NL | 45 | 47.2193 | 45 | 44.9231 | 0.1709%
| PL | 50 | 15.7672 | 14.9 | 14.8806 | 0.1301%
| NL | 50 | 52.4659 | 50 | 49.9397 | 0.1207%
| PL | 60 | 19.0476 | 18 | 18.0232 | -0.1291%
| NL | 60 | 63.0252 | 60 | 60.0359 | -0.05991%
| PL | 65 | 20.6568 | 19.5 | 19.5649 | -0.3327%
| NL | 65 | 68.3491 | 65 | 65.1264 | -0.1944%
| PL | 70 | 22.1398 | 20.9 | 20.986 | -0.4116%
| NL | 70 | 73.6842 | 70 | 70.2275 | -0.3249%
| PL | 80 | 25.4507 | 24 | 24.1577 | -0.6572%
| NL | 80 | 84.2993 | 80 | 80.377 | -0.4712%
| PL | 100 | 31.5789 | 30 | 30.0297 | -0.0989%
| NL | 100 | 104.9318 | 100 | 100.1052 | -0.1052%
| PL | 108 | 34.0336 | 32.4 | 32.3817 | 0.05659%
| NL | 108 | 113.089 | 108 | 107.9049 | 0.08802%
| PL | 120 | 37.6569 | 36 | 35.8536 | 0.4067%
| NL | 120 | 125.3918 | 120 | 119.6686 | 0.2762%
| k1 | k2 | k3
| 0.95532 | 0.00087501 | -0.22586
| L_min | 30%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.3 | 0.28747 |  |  | 1 | 0.9562

## Mid-Big Wood Chips Boiler v2
| Wood Chip Boiler | Size [kw_th] | eff (%) | ref eff, min load | input [kW_LHV]
| Decentralized Wood Chip Boiler PL | 45 | 92.4% | [183] | 48.7013 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 150 | 92.5% | [183] | 162.1622 | NL | 64.6104 | 59.7 | 215.1351 | 199
| Decentralized Wood Chip Boiler PL | 72 | 95.7% | [183] | 75.2351 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 240 | 95.8% | [183] | 250.5219 | NL | 78.0564 | 74.7 | 259.9165 | 249
| Decentralized Wood Chip Boiler PL | 72 | 95.7% | [183] | 75.2351 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 300 | 95.5% | [183] | 314.1361 | NL | 87.5235 | 83.76 | 365.445 | 349
| Decentralized Wood Chip Boiler PL | 119.7 | 95.7% | [184] | 125.0784 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 399 | 94.1% | [184] | 424.017 | NL | 140.7524 | 134.7 | 477.152 | 449
| Decentralized Wood Chip Boiler PL | 149.7 | 95.7% | [184] | 156.4263 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 499 | 93.4% | [184] | 534.2612 | NL | 156.4263 | 149.7 | 534.2612 | 499
| Decentralized Wood Chip Boiler PL | 180 | 92.5% | [185] | 194.5946 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 600 | 92.5% | [185] | 648.6486 | NL | 194.5946 | 180 | 648.6486 | 600
| Decentralized Wood Chip Boiler PL | 240 | 94.5% | [185] | 253.9683 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 800 | 93.2% | [185] | 858.3691 | NL | 253.9683 | 240 | 858.3691 | 800
| Decentralized Wood Chip Boiler PL | 300 | 94.5% | [185] | 317.4603 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 1000 | 91.1% | [185] | 1097.6948 | NL | 317.4603 | 300 | 1097.6948 | 1000
| Decentralized Wood Chip Boiler PL | 375 | 94.3% | [185] | 397.667 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 1250 | 93.4% | [185] | 1338.3298 | NL | 397.667 | 375 | 1338.3298 | 1250
| Decentralized Wood Chip Boiler PL | 450 | 94.3% | [185] | 477.2004 | PL | 1_WC | 1_Heat | 2_WC | 2_Heat
| Decentralized Wood Chip Boiler NL | 1500 | 92.6% | [185] | 1619.8704 | NL | 477.2004 | 450 | 1619.8704 | 1500
| Ref | Link
[183] | KWB Powerfire 1 - Wood chip biomass boiler | https://www.kwb.net/en/products/wood-heating-systems/wood-chip-boilers/kwb-powerfire/
[184] | KWB Powerfire 2 | https://www.kwb.net/en/products/wood-heating-systems/wood-chip-boilers/kwb-powerfire-2/
[185] | BioFire 500-1500 P45S | https://www.myriadproducts.co.uk/hubfs/Resource%20centre%20files/Biomass%20products%20-%20Datasheets/Datasheet%20BF%20500-1500kW%20P45S%20v1.0.pdf?hsLang=en
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 150 | 48.7013 | 45 | 48.41 | -7.578%
| NL | 150 | 162.1622 | 150 | 152.8403 | -1.894%
| PL | 240 | 75.2351 | 72 | 73.226 | -1.703%
| NL | 240 | 250.5219 | 240 | 234.5614 | 2.266%
| PL | 300 | 75.2351 | 72 | 73.4886 | -2.068%
| NL | 300 | 314.1361 | 300 | 293.3751 | 2.208%
| PL | 399 | 125.0784 | 119.7 | 119.7982 | -0.08205%
| NL | 399 | 424.017 | 399 | 394.9438 | 1.017%
| PL | 499 | 156.4263 | 149.7 | 149.0889 | 0.4082%
| NL | 499 | 534.2612 | 499 | 496.8513 | 0.4306%
| PL | 600 | 194.5946 | 180 | 184.6615 | -2.59%
| NL | 600 | 648.6486 | 600 | 602.5766 | -0.4294%
| PL | 800 | 253.9683 | 240 | 240.1851 | -0.07713%
| NL | 800 | 858.3691 | 800 | 796.4807 | 0.4399%
| PL | 1000 | 317.4603 | 300 | 299.4994 | 0.1669%
| NL | 1000 | 1097.6948 | 1000 | 1017.6337 | -1.763%
| PL | 1250 | 397.667 | 375 | 374.4168 | 0.1555%
| NL | 1250 | 1338.3298 | 1250 | 1240.2106 | 0.7832%
| PL | 1500 | 477.2004 | 450 | 448.7145 | 0.2857%
| NL | 1500 | 1619.8704 | 1500 | 1500.4375 | -0.02916%
| k1 | k2 | k3
| 0.92041 | 0.004378 | 2.9282
| L_min | 30%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.3 | 0.2805 |  |  | 1 | 0.92479

## Small Pellet Boiler v2
| Pellet Boiler | Size [kw_th] | eff (%) | ref eff, min load | input [kW_LHV]
| Decentralized Pellet Boiler PL | 3 | 93.2% | [141] | 3.2189 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 10 | 92.62% | [141] | 10.7968 | NL | 4.5064 | 4.2 | 15.1155 | 14
| Decentralized Pellet Boiler PL | 5 | 90% | [141] | 5.5556 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 15 | 93% | [141] | 16.129 | NL | 6.6667 | 6 | 19.3548 | 18
| Decentralized Pellet Boiler PL | 6 | 93.13% | [141] | 6.4426 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 20 | 92.9% | [141] | 21.5285 | NL | 9.6639 | 9 | 32.2928 | 30
| Decentralized Pellet Boiler PL | 12 | 94.8% | [140] | 12.6582 | PL
| Decentralized Pellet Boiler NL | 40 | 96.5% | [140] | 41.4508 | NL
| Decentralized Pellet Boiler PL | 13.5 | 94.9% | [140] | 14.2255 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 45 | 96.4% | [140] | 46.6805 | NL | 14.2255 | 13.5 | 46.6805 | 45
| Decentralized Pellet Boiler PL | 14.9 | 94.9% | [140] | 15.7007 | PL
| Decentralized Pellet Boiler NL | 49.5 | 96.3% | [140] | 51.4019 | NL
| Decentralized Pellet Boiler PL | 18 | 95.1% | [140] | 18.9274 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 60 | 96.1% | [140] | 62.435 | NL | 18.9274 | 18 | 62.435 | 60
| Decentralized Pellet Boiler PL | 19.5 | 95.2% | [140] | 20.4832 | PL
| Decentralized Pellet Boiler NL | 65 | 96.1% | [140] | 67.6379 | NL
| Decentralized Pellet Boiler PL | 20.9 | 95.2% | [140] | 21.9538 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 69.5 | 96% | [140] | 72.3958 | NL | 22.1117 | 21.0504 | 72.9167 | 70
| Decentralized Pellet Boiler PL | 24 | 95.4% | [140] | 25.1572 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 80 | 95.8% | [140] | 83.5073 | NL | 25.1572 | 24 | 83.5073 | 80
| Decentralized Pellet Boiler PL | 30 | 95.7% | [140] | 31.348 | PL | 1_Pellet | 1_Heat | 2_Pellet | 2_Heat
| Decentralized Pellet Boiler NL | 100 | 95.8% | [140] | 104.3841 | NL | 32.9154 | 31.5 | 109.6033 | 105
| Decentralized Pellet Boiler PL | 32.4 | 95.8% | [140] | 33.8205 | PL
| Decentralized Pellet Boiler NL | 108 | 95.7% | [140] | 112.8527 | NL
| Decentralized Pellet Boiler PL | 45 | 92.1% | [140] | 48.8599 | PL
| Decentralized Pellet Boiler NL | 150 | 93.2% | [140] | 160.9442 | NL
| Ref | Link
[140] | Wood chip & Pellet heating systems 20 – 150 kW - Technology & Planning 2025 | https://www.kwb.net/fileadmin/media/EN/Technik_Planung_Anleitungen_PDF/KWB_T_P_EN_04_2025_Modul_E_Wood_chip_and_pellet_Heatings_system_20-150_kW.pdf
[141] | Mini Bio NE | https://en.kostrzewa.com.pl/products/mini-bio-ne
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 10 | 3.2189 | 3 | 3.4163 | -13.88%
| NL | 10 | 10.7968 | 10 | 10.6321 | -6.321%
| PL | 15 | 5.5556 | 5 | 5.6034 | -12.07%
| NL | 15 | 16.129 | 15 | 15.6716 | -4.477%
| PL | 20 | 6.4426 | 6 | 6.4101 | -6.834%
| NL | 20 | 21.5285 | 20 | 20.775 | -3.875%
| PL | 40 | 12.6582 | 12 | 12.1767 | -1.473%
| NL | 40 | 41.4508 | 40 | 39.5933 | 1.017%
| PL | 45 | 14.2255 | 13.5 | 13.6311 | -0.9713%
| NL | 45 | 46.6805 | 45 | 44.5351 | 1.033%
| PL | 49.5 | 15.7007 | 14.9 | 15.0017 | -0.6825%
| NL | 49.5 | 51.4019 | 49.5 | 48.9967 | 1.017%
| PL | 60 | 18.9274 | 18 | 17.9944 | 0.03086%
| NL | 60 | 62.435 | 60 | 59.4228 | 0.962%
| PL | 65 | 20.4832 | 19.5 | 19.4379 | 0.3186%
| NL | 65 | 67.6379 | 65 | 64.3391 | 1.017%
| PL | 69.5 | 21.9538 | 20.9 | 20.804 | 0.4593%
| NL | 69.5 | 72.3958 | 69.5 | 68.8355 | 0.9562%
| PL | 80 | 25.1572 | 24 | 23.7746 | 0.9391%
| NL | 80 | 83.5073 | 80 | 79.3362 | 0.8298%
| PL | 100 | 31.348 | 30 | 29.5176 | 1.608%
| NL | 100 | 104.3841 | 100 | 99.0634 | 0.9366%
| PL | 108 | 33.8205 | 32.4 | 31.8112 | 1.817%
| NL | 108 | 112.8527 | 108 | 107.0665 | 0.8644%
| PL | 150 | 48.8599 | 45 | 45.8129 | -1.806%
| NL | 150 | 160.9442 | 150 | 152.5408 | -1.694%
| k1 | k2 | k3
| 0.95221 | -0.0075952 | 0.42724
| L_min | 30%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.3 | 0.27807 |  |  | 1 | 0.94462

## Mid-Big Pellet Boiler v2
| Pellet Boiler | Size [kw_th] | eff (%) | ref eff, min load | input [kW_LHV]
| Decentralized Pellet Boiler PL | 45 | 92.1% | [183] | 48.8599 | PL
| Decentralized Pellet Boiler NL | 150 | 93.2% | [183] | 160.9442 | NL
| Decentralized Pellet Boiler PL | 72 | 96.1% | [183] | 74.922 | PL
| Decentralized Pellet Boiler NL | 240 | 96% | [183] | 250 | NL
| Decentralized Pellet Boiler PL | 72 | 96.1% | [183] | 74.922 | PL
| Decentralized Pellet Boiler NL | 300 | 95.7% | [183] | 313.4796 | NL
| Decentralized Pellet Boiler PL | 119.7 | 91.8% | [184] | 130.3922 | PL
| Decentralized Pellet Boiler NL | 399 | 93.8% | [184] | 425.3731 | NL
| Decentralized Pellet Boiler PL | 149.7 | 91.9% | [184] | 162.8945 | PL
| Decentralized Pellet Boiler NL | 499 | 93.6% | [184] | 533.1197 | NL
| Ref | Link
[183] | KWB Powerfire 1 - Wood chip biomass boiler | https://www.kwb.net/en/products/wood-heating-systems/wood-chip-boilers/kwb-powerfire/
[184] | KWB Powerfire 2 | https://www.kwb.net/en/products/wood-heating-systems/wood-chip-boilers/kwb-powerfire-2/
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 150 | 48.8599 | 45 | 47.5496 | -5.666%
| NL | 150 | 160.9442 | 150 | 153.7015 | -2.468%
| PL | 240 | 74.922 | 72 | 70.828 | 1.628%
| NL | 240 | 250 | 240 | 236.6394 | 1.4%
| PL | 300 | 74.922 | 72 | 69.8918 | 2.928%
| NL | 300 | 313.4796 | 300 | 295.823 | 1.392%
| PL | 399 | 130.3922 | 119.7 | 120.8814 | -0.9869%
| NL | 399 | 425.3731 | 399 | 400.2495 | -0.3132%
| PL | 499 | 162.8945 | 149.7 | 150.1031 | -0.2693%
| NL | 499 | 533.1197 | 499 | 500.7329 | -0.3473%
| k1 | k2 | k3
| 0.94707 | -0.015603 | 3.6162

## Check Boiler Biomass
eff
NL 100% | 88.2%
PL 60% | 87.8% |  | rapporto eff_PL/eff_NL | 0.99546
Decentralized Wood Chip Boiler NL MODEL 1500 kW WOOD CHIPS
| Output [kW_th] | eff_th | Input [kW_th]
Decentralized Wood Chip Boiler PL | 450 | 94.3% | 477.2004
Decentralized Wood Chip Boiler PL | 900 | 92.18% | 976.3501
Decentralized Wood Chip Boiler NL | 1500 | 92.6% | 1619.8704
30% è minimo di modelli che ho trovato, ed efficienza è gia data, idem per 100%
Ma si può aggiungere punto 60%
Utilizzo metodo indiretto che ha errore molto più basso
https://task32.ieabioenergy.com/wp-content/uploads/sites/2/2017/03/IEA-_Verenum_2006_Efficiency.pdf
| Output [kW_th] | eff_th | Input [kW_th]
Decentralized Pellet Boiler PL | 149.7 | 91.9% | 162.8945
Decentralized Pellet Boiler PL | 299.4 | 93.18% | 321.3291
Decentralized Pellet Boiler NL | 499 | 93.6% | 533.1197

## ICE_Small
| ICE CHP | Out EE [kw_el] | Out Heat [kw_th] | eff_el [%] | eff_th [%] | ref eff, min load | input [kW_LHV] el | input [kW_LHV] th | input [kW_LHV] both
| ICE CHP PL | 5 | 14.0126 | 23.8% | 66.7% | [148] | 21.0084 | 21.0084 | 21.0084 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 10 | 21.6216 | 29.6% | 64% | [148] | 33.7838 | 33.7838 | 33.7838 | NL | 21.0084 | 14.0126 | 5 | 33.7838 | 21.6216 | 10
| ICE CHP PL | 5 | 14.0506 | 23.7% | 66.6% | [148] | 21.097 | 21.097 | 21.097 | PL
| ICE CHP NL | 12 | 25.0385 | 31.2% | 65.1% | [148] | 38.4615 | 38.4615 | 38.4615 | NL
| ICE CHP PL | 12.5 | 35.2733 | 24.7% | 69.7% | [148] | 50.6073 | 50.6073 | 50.6073 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 25 | 53.125 | 30.4% | 64.6% | [148] | 82.2368 | 82.2368 | 82.2368 | NL | 40.4858 | 28.2186 | 10 | 65.7895 | 42.5 | 20
| ICE CHP PL | 15 | 38.8868 | 26.5% | 68.7% | [148] | 56.6038 | 56.6038 | 56.6038 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 30 | 60.4762 | 31.5% | 63.5% | [148] | 95.2381 | 95.2381 | 95.2381 | NL | 56.6038 | 38.8868 | 15 | 95.2381 | 60.4762 | 30
| ICE CHP PL | 16.5 | 42.9 | 26.5% | 68.8% | [147] | 62.2642 | 62.3547 | 62.3295 | PL
| ICE CHP NL | 33 | 63.7 | 32.5% | 62.8% | [147] | 101.5385 | 101.4331 | 101.469 | NL
| ICE CHP PL | 25 | 62.3 | 27.2% | 67.7% | [147] | 91.9118 | 92.0236 | 91.9916 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 50 | 88.5 | 34.2% | 60.6% | [147] | 146.1988 | 146.0396 | 146.097 | NL | 91.9118 | 62.2243 | 25 | 146.1988 | 88.5965 | 50
| Ref | Link
[147] | The tests of micro-CHP prototype with SI engine powered by LPG and natural gas | https://www.combustion-engines.eu/pdf-142951-74319?filename=The+tests+of+micro_CHP.pdf
[148] | Totem Datasheets | https://www.totem.energy/totem_gamma/
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 10 | 21.0084 | 5 | 14.0126 | 5.1742 | 14.199 | -3.484% | -1.33%
| NL | 10 | 33.7838 | 10 | 21.6216 | 10.1385 | 21.5182 | -1.385% | 0.4781%
| PL | 12 | 21.097 | 5 | 14.0506 | 4.7588 | 14.6975 | 4.824% | -4.604%
| NL | 12 | 38.4615 | 12 | 25.0385 | 11.5063 | 24.6459 | 4.114% | 1.568%
| PL | 25 | 50.6073 | 12.5 | 35.2733 | 13.3019 | 34.5147 | -6.416% | 2.151%
| NL | 25 | 82.2368 | 25 | 53.125 | 25.5927 | 52.6359 | -2.371% | 0.9207%
| PL | 30 | 56.6038 | 15 | 38.8868 | 14.5074 | 39.0695 | 3.284% | -0.4699%
| NL | 30 | 95.2381 | 30 | 60.4762 | 29.5201 | 61.2038 | 1.6% | -1.203%
| PL | 33 | 62.3295 | 16.5173 | 42.8827 | 16.0576 | 43.0215 | 2.783% | -0.3236%
| NL | 33 | 101.469 | 32.9774 | 63.7226 | 31.2666 | 65.4453 | 5.188% | -2.703%
| PL | 50 | 91.9916 | 25.0217 | 62.2783 | 23.76 | 63.8211 | 5.042% | -2.477%
| NL | 50 | 146.097 | 49.9652 | 88.5348 | 44.7845 | 94.8191 | 10.37% | -7.098%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.38858 | -0.22493 | -0.74004 |  | 0.57292 | 0.22386 | -0.075747
| 0.38858 | -0.22493 | -0.74004 |  | 0.57292 | 0.22386 | -0.075747
| L_min | 50%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.5 | -0.030634 | 0.51032 |  | 1 | 0.16366 | 0.79678

## Check ICE small
Tutte le taglie da ref 148 presentano profili lineari
(Pot in ingresso = Input, Carico El = Output)
| Modello 10 |  |  |  |  | Modello 30
Per quelli da ref 147:
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 1 | 12.5% | [147] | 8 | PL
ICE CHP PL | 2 | 20.5% | [147] | 9.7561 | PL
ICE CHP PL | 3 | 25.5% | [147] | 11.7647 | PL
ICE CHP PL | 4 | 28% | [147] | 14.2857 | PL
ICE CHP NL | 5 | 29% | [147] | 17.2414 | NL
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 10 | 12.5% | [147] | 80 | PL
ICE CHP PL | 20 | 20.5% | [147] | 97.561 | PL
ICE CHP PL | 30 | 25.5% | [147] | 117.6471 | PL
ICE CHP PL | 40 | 28% | [147] | 142.8571 | PL
ICE CHP NL | 50 | 29% | [147] | 172.4138 | NL

## ICE_Mid
| ICE CHP | Out EE [kw_el] | Out Heat [kw_th] | eff_el [%] | eff_th [%] | ref eff, min load | input [kW_LHV] el | input [kW_LHV] th | input [kW_LHV] both
| ICE CHP PL | 42 | 82 | 28.6% | 55.7% | [147] | 146.8531 | 147.2172 | 147.0937 | PL
| ICE CHP NL | 70 | 109 | 34.3% | 53.4% | [147] | 204.0816 | 204.1199 | 204.1049 | NL
| ICE CHP PL | 42.5 | 98 | 27.1% | 62.8% | [147] | 156.8266 | 156.051 | 156.2848 | PL
| ICE CHP NL | 85 | 141 | 33.7% | 56.1% | [147] | 252.2255 | 251.3369 | 251.6704 | NL
| ICE CHP PL | 52 | 112 | 28.6% | 61.5% | [147] | 181.8182 | 182.1138 | 182.02 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 104 | 166 | 34.7% | 55.3% | [147] | 299.7118 | 300.1808 | 300 | NL | 174.8252 | 107.5175 | 50 | 288.1844 | 159.366 | 100
| ICE CHP PL | 62 | 119 | 31% | 59.3% | [147] | 200 | 200.6745 | 200.443 | PL
| ICE CHP NL | 124 | 182 | 36.6% | 53.6% | [147] | 338.7978 | 339.5522 | 339.2461 | NL
| ICE CHP PL | 66.5 | 129 | 30.6% | 59.5% | [147] | 217.3203 | 216.8067 | 216.9811 | PL
| ICE CHP NL | 133 | 191 | 37.8% | 54.2% | [147] | 351.8519 | 352.3985 | 352.1739 | NL
| ICE CHP PL | 82 | 134 | 33.2% | 54.3% | [147] | 246.988 | 246.7772 | 246.8571 | PL
| ICE CHP NL | 164 | 209 | 37.8% | 48.2% | [147] | 433.8624 | 433.61 | 433.7209 | NL
| ICE CHP PL | 92 | 136 | 35.2% | 52.1% | [147] | 261.3636 | 261.0365 | 261.1684 | PL
| ICE CHP NL | 184 | 218 | 39.2% | 46.5% | [147] | 469.3878 | 468.8172 | 469.0782 | NL
| ICE CHP PL | 100 | 147 | 35.3% | 52.1% | [147] | 283.2861 | 282.1497 | 282.6087 | PL
| ICE CHP NL | 200 | 237 | 39.2% | 46.5% | [147] | 510.2041 | 509.6774 | 509.9183 | NL
| ICE CHP PL | 105 | 149 | 35.7% | 50.7% | [147] | 294.1176 | 293.8856 | 293.9815 | PL
| ICE CHP NL | 210 | 248 | 39.7% | 46.9% | [147] | 528.9673 | 528.7846 | 528.8684 | NL
| Ref | Link
[147] | ShentonGroup Datasheets & Technical Drawings | https://www.shentongroup.co.uk/tech-info/datasheets
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 70 | 147.0937 | 42.0688 | 81.9312 | 39.2623 | 95.7256 | 6.671% | -16.84%
| NL | 70 | 204.1049 | 70.008 | 108.992 | 64.7169 | 119.613 | 7.558% | -9.745%
| PL | 85 | 156.2848 | 42.3532 | 98.1468 | 43.2789 | 98.8918 | -2.186% | -0.759%
| NL | 85 | 251.6704 | 84.8129 | 141.1871 | 85.8671 | 138.858 | -1.243% | 1.65%
| PL | 104 | 182.02 | 52.0577 | 111.9423 | 54.659 | 108.8074 | -4.997% | 2.8%
| NL | 104 | 300 | 104.1 | 165.9 | 107.3353 | 158.2406 | -3.108% | 4.617%
| PL | 124 | 200.443 | 62.1373 | 118.8627 | 62.7685 | 115.6135 | -1.016% | 2.734%
| NL | 124 | 339.2461 | 124.1641 | 181.8359 | 124.742 | 173.7715 | -0.4654% | 4.435%
| PL | 133 | 216.9811 | 66.3962 | 129.1038 | 70.1003 | 122.1321 | -5.579% | 5.4%
| NL | 133 | 352.1739 | 133.1217 | 190.8783 | 130.4618 | 178.7774 | 1.998% | 6.34%
| PL | 164 | 246.8571 | 81.9566 | 134.0434 | 83.2596 | 133.2348 | -1.59% | 0.6032%
| NL | 164 | 433.7209 | 163.9465 | 209.0535 | 166.6914 | 211.5301 | -1.674% | -1.185%
| PL | 184 | 261.1684 | 91.9313 | 136.0687 | 89.5332 | 138.3182 | 2.609% | -1.653%
| NL | 184 | 469.0782 | 183.8786 | 218.1214 | 182.3618 | 225.4316 | 0.8249% | -3.351%
| PL | 200 | 282.6087 | 99.7609 | 147.2391 | 99.0131 | 146.5711 | 0.7495% | 0.4537%
| NL | 200 | 509.9183 | 199.888 | 237.112 | 200.5034 | 241.8131 | -0.3079% | -1.983%
| PL | 210 | 293.9815 | 104.9514 | 149.0486 | 104.0329 | 150.8798 | 0.8752% | -1.229%
| NL | 210 | 528.8684 | 209.9607 | 248.0393 | 208.9063 | 249.2965 | 0.5022% | -0.5069%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.44648 | -0.0058041 | -26.0065 |  | 0.419 | -0.045652 | 37.2894
| 0.44648 | -0.0058041 | -26.0065 |  | 0.419 | -0.045652 | 37.2894
| L_min | 50%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.5 | 0.21744 | 0.16385 |  | 1 | 0.44068 | 0.37334

## ICE_Large
| ICE CHP | Out EE [kw_el] | Out Heat [kw_th] | eff_el [%] | eff_th [%] | ref eff, min load | input [kW_LHV] el | input [kW_LHV] th | input [kW_LHV] both
| ICE CHP PL | 130 | 238 | 32.4% | 59.4% | [147] | 401.2346 | 400.6734 | 400.8715 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 260 | 370 | 38% | 54% | [147] | 684.2105 | 685.1852 | 684.7826 | NL | 462.963 | 275 | 150 | 789.4737 | 426.3158 | 300
| ICE CHP PL | 177 | 248 | 37.5% | 52.5% | [147] | 472 | 472.381 | 472.2222 | PL
| ICE CHP NL | 354 | 440 | 40% | 49.8% | [147] | 885 | 883.5341 | 884.1871 | NL
| ICE CHP PL | 215 | 324 | 35.9% | 54.1% | [147] | 598.8858 | 598.8909 | 598.8889 | PL
| ICE CHP NL | 430 | 545 | 39.6% | 50.2% | [147] | 1085.8586 | 1085.6574 | 1085.7461 | NL
| ICE CHP PL | 264 | 365 | 37.4% | 51.7% | [147] | 705.8824 | 705.9961 | 705.9484 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 528 | 641 | 40.5% | 49.2% | [147] | 1303.7037 | 1302.8455 | 1303.233 | NL | 668.4492 | 345.5882 | 250 | 1234.5679 | 607.4074 | 500
| ICE CHP PL | 300 | 372 | 38.9% | 48.2% | [147] | 771.2082 | 771.7842 | 771.527 | PL
| ICE CHP NL | 600 | 644 | 42.3% | 45.4% | [147] | 1418.4397 | 1418.5022 | 1418.4721 | NL
| ICE CHP PL | 400 | 497 | 39% | 48.5% | [147] | 1025.641 | 1024.7423 | 1025.1429 | PL
| ICE CHP NL | 800 | 856 | 42.5% | 45.5% | [147] | 1882.3529 | 1881.3187 | 1881.8182 | NL
| ICE CHP PL | 499.5 | 655 | 37.7% | 49.4% | [147] | 1324.9337 | 1325.9109 | 1325.4879 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 999 | 1102 | 42% | 46.3% | [147] | 2378.5714 | 2380.1296 | 2379.3884 | NL | 1326.2599 | 655.1724 | 500 | 2380.9524 | 1102.381 | 1000
| ICE CHP PL | 600 | 731 | 39.2% | 47.8% | [147] | 1530.6122 | 1529.2887 | 1529.8851 | PL
| ICE CHP NL | 1200 | 1245 | 42.6% | 44.2% | [147] | 2816.9014 | 2816.7421 | 2816.8203 | NL
| ICE CHP PL | 780 | 963 | 39% | 48.2% | [147] | 2000 | 1997.9253 | 1998.8532 | PL
| ICE CHP NL | 1560 | 1650 | 42.2% | 44.6% | [147] | 3696.6825 | 3699.5516 | 3698.1567 | NL
| ICE CHP PL | 1000 | 1184 | 39.5% | 46.8% | [147] | 2531.6456 | 2529.9145 | 2530.7068 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| ICE CHP NL | 2000 | 2001 | 43.4% | 43.4% | [147] | 4608.2949 | 4610.5991 | 4609.447 | NL | 2531.6456 | 1184.8101 | 1000 | 4608.2949 | 2000 | 2000
| Ref | Link
[147] | ShentonGroup Datasheets & Technical Drawings | https://www.shentongroup.co.uk/tech-info/datasheets
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 260 | 400.8715 | 129.8824 | 238.1176 | 135.9009 | 236.5874 | -4.634% | 0.6426%
| NL | 260 | 684.7826 | 260.2174 | 369.7826 | 268.8724 | 352.281 | -3.326% | 4.733%
| PL | 354 | 472.2222 | 177.0833 | 247.9167 | 162.3353 | 269.6256 | 8.328% | -8.757%
| NL | 354 | 884.1871 | 353.6748 | 440.3252 | 355.2814 | 437.5009 | -0.4542% | 0.6414%
| PL | 430 | 598.8889 | 215.0011 | 323.9989 | 216.0143 | 324.446 | -0.4713% | -0.138%
| NL | 430 | 1085.7461 | 429.9555 | 545.0445 | 444.0367 | 522.8399 | -3.275% | 4.074%
| PL | 528 | 705.9484 | 264.0247 | 364.9753 | 258.8759 | 372.2041 | 1.95% | -1.981%
| NL | 528 | 1303.233 | 527.8094 | 641.1906 | 538.6176 | 615.597 | -2.048% | 3.992%
| PL | 600 | 771.527 | 300.124 | 371.876 | 284.2412 | 401.9626 | 5.292% | -8.09%
| NL | 600 | 1418.4721 | 600.0137 | 643.9863 | 587.2416 | 665.5921 | 2.129% | -3.355%
| PL | 800 | 1025.1429 | 399.8057 | 497.1943 | 388.1657 | 513.7422 | 2.911% | -3.328%
| NL | 800 | 1881.8182 | 799.7727 | 856.2273 | 789.3945 | 862.8367 | 1.298% | -0.7719%
| PL | 999 | 1325.4879 | 499.709 | 654.791 | 514.0505 | 644.5218 | -2.87% | 1.568%
| NL | 999 | 2379.3884 | 999.3431 | 1101.6569 | 1007.6508 | 1073.9853 | -0.8313% | 2.512%
| PL | 1200 | 1529.8851 | 599.7149 | 731.2851 | 594.8488 | 736.2869 | 0.8114% | -0.684%
| NL | 1200 | 2816.8203 | 1199.9654 | 1245.0346 | 1197.5924 | 1260.7119 | 0.1978% | -1.259%
| PL | 1560 | 1998.8532 | 779.5528 | 963.4472 | 787.7485 | 942.5675 | -1.051% | 2.167%
| NL | 1560 | 3698.1567 | 1560.6221 | 1649.3779 | 1583.6271 | 1635.0322 | -1.474% | 0.8698%
| PL | 2000 | 2530.7068 | 999.6292 | 1184.3708 | 1004.1579 | 1177.8464 | -0.453% | 0.5509%
| NL | 2000 | 4609.447 | 2000.5 | 2000.5 | 1977.7478 | 2024.9313 | 1.137% | -1.221%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.46836 | -0.074289 | -32.5343 |  | 0.4075 | 0.042157 | 62.2719
| 0.46836 | -0.074289 | -32.5343 |  | 0.4075 | 0.042157 | 62.2719
| L_min | 50%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.5 | 0.15989 | 0.24591 |  | 1 | 0.39407 | 0.44966

## Check ICE Mid-Large
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 3 | 28.6% | [147] | 10.4895 | PL
ICE CHP PL | 3.75 | 33% | [147] | 11.3636 | PL
ICE CHP NL | 5 | 34.3% | [147] | 14.5773 | NL
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 42.5 | 27.1% | [147] | 156.8266 | PL
ICE CHP PL | 63.75 | 31% | [147] | 205.6452 | PL
ICE CHP NL | 85 | 33.7% | [147] | 252.2255 | NL
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 66.5 | 30.6% | [147] | 217.3203 | PL
ICE CHP PL | 99.75 | 35.5% | [147] | 280.9859 | PL
ICE CHP NL | 133 | 37.8% | [147] | 351.8519 | NL
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 105 | 35.7% | [147] | 294.1176 | PL
ICE CHP PL | 157.5 | 38.6% | [147] | 408.0311 | PL
ICE CHP NL | 210 | 39.7% | [147] | 528.9673 | NL
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 130 | 32.4% | [147] | 401.2346 | PL
ICE CHP PL | 195 | 36.4% | [147] | 535.7143 | PL
ICE CHP NL | 260 | 38% | [147] | 684.2105 | NL
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 300 | 38.9% | [147] | 771.2082 | PL
ICE CHP PL | 450 | 41.2% | [147] | 1092.233 | PL
ICE CHP NL | 600 | 42.3% | [147] | 1418.4397 | NL
ICE CHP | Out EE [kw_el] | eff_el [%] | ref eff, min load | input [kW_LHV] el
ICE CHP PL | 1000 | 39.5% | [147] | 2531.6456 | PL
ICE CHP PL | 1500 | 42.3% | [147] | 3546.0993 | PL
ICE CHP NL | 2000 | 43.4% | [147] | 4608.2949 | NL

## ORC biomass v2 small
| biomass ORC | Out EE [Mw_el] | Out Heat [Mw_th] | eff_el [%] | eff_th [%] | ref eff, min load | input [MW_LHV] | HP? | eff tot [%]
| biomass ORC PL | 0.0964 | 1.051 | 7.981% | 87.02% | [149][189] | 1.2078 | HP1 | 95% | PL | 1_Biom | 1_Heat | 1_EE | 2_Biom | 2_Heat | 2_EE
| biomass ORC NL | 0.964 | 4.142 | 17.94% | 77.06% | [150][189] | 5.3747 |  | 95% | NL | 1.2529 | 1.0903 | 0.1 | 5.5755 | 4.2967 | 1
| biomass ORC PL | 0.1236 | 1.3762 | 7.829% | 87.17% | [149][189] | 1.5787 | HP1 | 95% | PL
| biomass ORC NL | 1.236 | 5.438 | 17.59% | 77.41% | [150][189] | 7.0253 |  | 95% | NL
| biomass ORC PL | 0.175 | 2.061 | 7.435% | 87.56% | [149][189] | 2.3536 | HP1 | 95% | PL
| biomass ORC NL | 1.75 | 8.2 | 16.71% | 78.29% | [151][189] | 10.4737 |  | 95% | NL
| biomass ORC PL | 0.1862 | 1.9965 | 8.104% | 86.9% | [149][189] | 2.2976 | HP1 | 95% | PL
| biomass ORC NL | 1.862 | 7.851 | 18.21% | 76.79% | [150][189] | 10.2242 |  | 95% | NL
| Ref | Link | [6 empty] | HP1 | total eff PL = total eff NL
[149] | Turboden | https://ee-ip.org/fileadmin/user_upload/DOCUMENTS/Content/15-COM.P-7-rev.7.pdf
[150] | Turboden: ORC Solutions for Cogeneration and District Heating | https://iea.blob.core.windows.net/assets/imports/events/122/Alessandro_Foresti_2015_03_23_Kiev.pdf
[151] | Turboden References | https://www.turboden.com/references
[189] | Biomass-fired Organic Rankine Cycle combined heat and power systems - A. Guercio, R. Bini
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 0.964 | 1.2078 | 0.0964 | 1.051 | 0.099889 | 1.0475 | -3.62% | 0.332%
| NL | 0.964 | 5.3747 | 0.964 | 4.142 | 0.94425 | 4.1618 | 2.049% | -0.4768%
| PL | 1.236 | 1.5787 | 0.1236 | 1.3762 | 0.12903 | 1.3707 | -4.392% | 0.3945%
| NL | 1.236 | 7.0253 | 1.236 | 5.438 | 1.2327 | 5.4413 | 0.2684% | -0.061%
| PL | 1.75 | 2.3536 | 0.175 | 2.061 | 0.19909 | 2.0369 | -13.77% | 1.169%
| NL | 1.75 | 10.4737 | 1.75 | 8.2 | 1.8445 | 8.1055 | -5.399% | 1.152%
| PL | 1.862 | 2.2976 | 0.1862 | 1.9965 | 0.16878 | 2.0139 | 9.353% | -0.8723%
| NL | 1.862 | 10.2242 | 1.862 | 7.851 | 1.775 | 7.938 | 4.673% | -1.108%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.20263 | -0.16919 | 0.018243 |  | 0.74737 | 0.16919 | -0.018243
| 0.20263 | -0.16919 | 0.018243 |  | 0.74737 | 0.16919 | -0.018243
| L_min | 10%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.1 | -0.14892 | 0.24392 |  | 1 | 0.033447 | 0.91655
fonti
https://ee-ip.org/fileadmin/user_upload/DOCUMENTS/Content/15-COM.P-7-rev.7.pdf
https://www.turboden.com/products/2463/orc-system

## ORC biomass v2 big
| biomass ORC | Out EE [Mw_el] | Out Heat [Mw_th] | eff_el [%] | eff_th [%] | ref eff, min load | input [MW_LHV] | HP? | eff tot [%]
| biomass ORC PL | 0.2 | 2.4966 | 7.046% | 87.95% | [149][189] | 2.8386 | HP1 | 95% | PL
| biomass ORC NL | 2 | 10 | 15.83% | 79.17% | [150][189] | 12.6316 |  | 95% | NL
| biomass ORC PL | 0.21 | 2.4754 | 7.429% | 87.57% | [149][189] | 2.8267 | HP1 | 95% | PL
| biomass ORC NL | 2.1 | 9.85 | 16.69% | 78.31% | [151][189] | 12.5789 |  | 95% | NL
| biomass ORC PL | 0.3 | 3.5831 | 7.339% | 87.66% | [149][189] | 4.0875 | HP1 | 95% | PL | 1_Biom | 1_Heat | 1_EE | 2_Biom | 2_Heat | 2_EE
| biomass ORC NL | 3 | 14.28 | 16.49% | 78.51% | [150][189] | 18.1895 |  | 95% | NL | 13.6251 | 11.9438 | 1 | 60.6316 | 47.6 | 10
| Ref | Link | [6 empty] | HP1 | total eff PL = total eff NL
[149] | Turboden | https://ee-ip.org/fileadmin/user_upload/DOCUMENTS/Content/15-COM.P-7-rev.7.pdf
[150] | Turboden: ORC Solutions for Cogeneration and District Heating | https://iea.blob.core.windows.net/assets/imports/events/122/Alessandro_Foresti_2015_03_23_Kiev.pdf
[151] | Turboden References | https://www.turboden.com/references
[189] | Biomass-fired Organic Rankine Cycle combined heat and power systems - A. Guercio, R. Bini
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 2 | 2.8386 | 0.2 | 2.4966 | 0.20466 | 2.492 | -2.332% | 0.1868%
| NL | 2 | 12.6316 | 2 | 10 | 2.0653 | 9.9347 | -3.267% | 0.6535%
| PL | 2.1 | 2.8267 | 0.21 | 2.4754 | 0.18964 | 2.4958 | 9.695% | -0.8225%
| NL | 2.1 | 12.5789 | 2.1 | 9.85 | 2.0426 | 9.9074 | 2.735% | -0.583%
| PL | 3 | 4.0875 | 0.3 | 3.5831 | 0.3142 | 3.5689 | -4.733% | 0.3962%
| NL | 3 | 18.1895 | 3 | 14.28 | 2.9936 | 14.2864 | 0.214% | -0.04495%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.19 | -0.12777 | -0.079123 |  | 0.76 | 0.12777 | 0.079123
| 0.19 | -0.12777 | -0.079123 |  | 0.76 | 0.12777 | 0.079123
| L_min | 10%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.1 | -0.10877 | 0.20377 |  | 1 | 0.06223 | 0.88777
fonti
https://ee-ip.org/fileadmin/user_upload/DOCUMENTS/Content/15-COM.P-7-rev.7.pdf
https://www.turboden.com/products/2463/orc-system

## Check ORC biomass
PL | effPL/effNL
10% | 0.445
20% | 0.675
30% | 0.778
40% | 0.862
50% | 0.92
60% | 0.96
70% | 0.982
80% | 0.995
90% | 0.998
100% | 1
biomass ORC | Out EE [Mw_el] | eff_el [%] | ref eff, min load | input [MW_LHV]
biomass ORC PL | 0.3 | 7.34% | [149] | 4.0874
biomass ORC PL | 0.6 | 11.13% | [149] | 5.3893
biomass ORC PL | 0.9 | 12.83% | [149] | 7.0138
biomass ORC PL | 1.2 | 14.22% | [149] | 8.4404
biomass ORC PL | 1.5 | 15.17% | [149] | 9.8853
biomass ORC PL | 1.8 | 15.83% | [149] | 11.3681
biomass ORC PL | 2.1 | 16.2% | [149] | 12.9657
biomass ORC PL | 2.4 | 16.41% | [149] | 14.6243
biomass ORC PL | 2.7 | 16.46% | [149] | 16.4029
biomass ORC NL | 3 | 16.49% | [151] | 18.189

## SOFC CHP v2 Small
| SOFC CHP | Out EE [kw_el] | Out Heat [kw_th] | eff_el [%] | eff_th [%] | eff_tot [%] | ref eff, min load | input [kW_LHV]
| SOFC CHP PL | 0.5 | 0.69545 | 37.64% | 52.36% | 90% | [158][156][190][191] | 1.3283 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| SOFC CHP NL | 1.5 | 0.86842 | 57% | 33% | 90% | [158][156][190][191] | 2.6316 | NL | 1.3283 | 0.69545 | 0.5 | 2.6316 | 0.86842 | 1.5
| SOFC CHP PL | 5 | 28.3329 | 13.5% | 76.5% | 90% | [156][190][191] | 37.0366 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| SOFC CHP NL | 50 | 34.9057 | 53% | 37% | 90% | [156][190][191] | 94.3396 | NL | 37.0366 | 28.3329 | 5 | 94.3396 | 34.9057 | 50
| Ref | Link | [6 empty] | Note
[156] | Efficiency analysis of 50 kWe SOFC systems fueled with biogas from waste water | https://www.researchgate.net/publication/341720840_Efficiency_analysis_of_50_kWe_SOFC_systems_fueled_with_biogas_from_waste_water
[157] | Convion C60 | https://convion.fi/wp-content/uploads/2023/09/Convion_C60_brochure_2023.pdf
[158] | BLUEGEN -15 | https://bluegen.eu/wp-content/uploads/2022/09/Brochure_Bluegen_ENG_2022-09_v3_acc.pdf
[159] | The Bloom Energy Server 6.5 | https://www.bloomenergy.com/wp-content/uploads/bloom-energy-server-datasheet-2024.pdf
[160] | Solid oxide fuel cell hybrid system: a detailed review of an environmentally clean and efficient source of energy | https://unige.iris.cineca.it/bitstream/11567/932321/1/1-s2.0-S0360544218323028-main.pdf
[190] | Establishment of a High Efficiency Electric Power System-- INER's 1 kW Solid Oxide Fuel Cell Power System | https://www.nusc.gov.tw/english/About-NSC/Establishment-of-a-High-Efficiency-Electric-Power-System-INER-s-1-kW-Solid-Oxide-Fuel-Cell-Power-System-20080811-195.html
[191] | Thermal-electric cogeneration efficiency of 92.55% ranks first in the world. | https://www.prnewswire.com/news-releases/thermal-electric-cogeneration-efficiency-of-92-55-ranks-first-in-the-world-weichai-releases-the-worlds-first-commercialized-high-power-metal-supported-sofc-product-301762592.html
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 1.5 | 1.3283 | 0.5 | 0.69545 | 0.48826 | 0.70718 | 2.347% | -1.687%
| NL | 1.5 | 2.6316 | 1.5 | 0.86842 | 1.5117 | 0.85669 | -0.7824% | 1.351%
| PL | 50 | 37.0366 | 5 | 28.3329 | 5.0003 | 28.3327 | -0.005338% | 0.000942%
| NL | 50 | 94.3396 | 50 | 34.9057 | 49.9997 | 34.9059 | 0.0005338% | -0.0007647%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.78529 | -0.48514 | 0.1729 |  | 0.11471 | 0.48514 | -0.1729
| 0.78529 | -0.48514 | 0.1729 |  | 0.11471 | 0.48514 | -0.1729
| L_min | 10%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.1 | -0.40661 | 0.49661 |  | 1 | 0.30015 | 0.59985
https://www.researchgate.net/publication/341720840_Efficiency_analysis_of_50_kWe_SOFC_systems_fueled_with_biogas_from_waste_water

## SOFC CHP v2 Big
| SOFC CHP | Out EE [kw_el] | Out Heat [kw_th] | eff_el [%] | eff_th [%] | eff_tot [%] | ref eff, min load | input [kW_LHV]
| SOFC CHP PL | 25 | 135.6042 | 14.01% | 75.99% | 90% | [156][190][191] | 178.4491 | PL
| SOFC CHP NL | 250 | 159.0909 | 55% | 35% | 90% | [160][156] | 454.5455 | NL
| SOFC CHP PL | 32.5 | 184.1641 | 13.5% | 76.5% | 90% | [156][190][191] | 240.7379 | PL | 1_NG | 1_Heat | 1_EE | 2_NG | 2_Heat | 2_EE
| SOFC CHP NL | 325 | 226.8868 | 53% | 37% | 90% | [160][156] | 613.2075 | NL | 370.366 | 283.3294 | 50 | 943.3962 | 349.0566 | 500
| Ref | Link | [6 empty] | Note
[156] | Efficiency analysis of 50 kWe SOFC systems fueled with biogas from waste water | https://www.researchgate.net/publication/341720840_Efficiency_analysis_of_50_kWe_SOFC_systems_fueled_with_biogas_from_waste_water
[157] | Convion C60 | https://convion.fi/wp-content/uploads/2023/09/Convion_C60_brochure_2023.pdf
[158] | BLUEGEN -15 | https://bluegen.eu/wp-content/uploads/2022/09/Brochure_Bluegen_ENG_2022-09_v3_acc.pdf
[159] | The Bloom Energy Server 6.5 | https://www.bloomenergy.com/wp-content/uploads/bloom-energy-server-datasheet-2024.pdf
[160] | Solid oxide fuel cell hybrid system: a detailed review of an environmentally clean and efficient source of energy | https://unige.iris.cineca.it/bitstream/11567/932321/1/1-s2.0-S0360544218323028-main.pdf
[190] | Establishment of a High Efficiency Electric Power System-- INER's 1 kW Solid Oxide Fuel Cell Power System | https://www.nusc.gov.tw/english/About-NSC/Establishment-of-a-High-Efficiency-Electric-Power-System-INER-s-1-kW-Solid-Oxide-Fuel-Cell-Power-System-20080811-195.html
[191] | Thermal-electric cogeneration efficiency of 92.55% ranks first in the world. | https://www.prnewswire.com/news-releases/thermal-electric-cogeneration-efficiency-of-92-55-ranks-first-in-the-world-weichai-releases-the-worlds-first-commercialized-high-power-metal-supported-sofc-product-301762592.html
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 250 | 178.4491 | 25 | 135.6042 | 27.6402 | 132.9639 | -10.56% | 1.947%
| NL | 250 | 454.5455 | 250 | 159.0909 | 247.3598 | 161.7311 | 1.056% | -1.66%
| PL | 325 | 240.7379 | 32.5 | 184.1641 | 30.5429 | 186.1212 | 6.022% | -1.063%
| NL | 325 | 613.2075 | 325 | 226.8868 | 326.9571 | 224.9297 | -0.6022% | 0.8626%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.79581 | -0.62223 | 41.1864 |  | 0.10419 | 0.62223 | -41.1864
| 0.79581 | -0.62223 | 41.1864 |  | 0.10419 | 0.62223 | -41.1864
| L_min | 10%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.1 | -0.54265 | 0.63265 |  | 1 | 0.17358 | 0.72642
https://www.researchgate.net/publication/341720840_Efficiency_analysis_of_50_kWe_SOFC_systems_fueled_with_biogas_from_waste_water

## Check SOFC CHP
PL | Load | el eff | Ratio eff_minPL/eff_NL
10% | 5 | 13.5% | 0.25472 | 0.25472
20% | 10 | 25% | 0.4717
30% | 15 | 35% | 0.66038
40% | 20 | 42.5% | 0.80189
50% | 25 | 49.5% | 0.93396
60% | 30 | 53.5% | 1.0094
70% | 35 | 55.5% | 1.0472
80% | 40 | 56.5% | 1.066
90% | 45 | 55% | 1.0377
100% | 50 | 53% | 1
SOFC CHP | Out EE [kw_el] | eff_el [%] | input [MW_LHV]
SOFC CHP PL | 25 | 14.01% | 178.4512
SOFC CHP PL | 50 | 25.94% | 192.7273
SOFC CHP PL | 75 | 36.32% | 206.4935
SOFC CHP PL | 100 | 44.1% | 226.738
SOFC CHP PL | 125 | 51.37% | 243.3425
SOFC CHP PL | 150 | 55.52% | 270.1784
SOFC CHP PL | 175 | 57.59% | 303.8493
SOFC CHP PL | 200 | 58.63% | 341.1102
SOFC CHP PL | 225 | 57.08% | 394.2149
SOFC CHP NL | 250 | 55% | 454.5455

## PEMFC CHP v2 small
| PEMFC CHP | Out EE [kw_el] | Out Heat [kw_th] | eff_el [%] | eff_th [%] | eff_tot [%] | ref eff, min load | input [kW_LHV]
| PEM FC CHP PL | 0.8 | 0.89412 | 42.5% | 47.5% | 90% | [163] | 1.8824 | PL | 1_H2 | 1_Heat | 1_EE | 2_H2 | 2_Heat | 2_EE
| PEM FC CHP NL | 5 | 5.7143 | 42% | 48% | 90% | [163] | 11.9048 | NL | 1.8824 | 0.89412 | 0.8 | 11.9048 | 5.7143 | 5
| PEM FC CHP PL | 15 | 10.0929 | 53.8% | 36.2% | 90% | [163] | 27.881 | PL
| PEM FC CHP NL | 60 | 60 | 45% | 45% | 90% | [163] | 133.3333 | NL
| Ref | Link
[163] | Zero-Emission Power Generation Solutions | https://powercellgroup.com/segments/power-generation/
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 5 | 1.8824 | 0.8 | 0.89412 | 0.7619 | 0.93222 | 4.763% | -4.262%
| NL | 5 | 11.9048 | 5 | 5.7143 | 5.0381 | 5.6762 | -0.7621% | 0.6668%
| PL | 60 | 27.881 | 15 | 10.0929 | 15.0036 | 10.0893 | -0.02414% | 0.03588%
| NL | 60 | 133.3333 | 60 | 60 | 59.9964 | 60.0036 | 0.006036% | -0.006036%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.42666 | 0.057255 | -0.32751 |  | 0.47334 | -0.057255 | 0.32751
| 0.42666 | 0.057255 | -0.32751 |  | 0.47334 | -0.057255 | 0.32751
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.15 | 0.12125 | 0.013746 |  | 1 | 0.48392 | 0.41608
https://ecp.ep.liu.se/index.php/sims/article/download/515/475/437

## PEMFC CHP v2 mid-big
| PEMFC CHP | Out EE [kw_el] | Out Heat [kw_th] | eff_el [%] | eff_th [%] | eff_tot [%] | ref eff, min load | input [kW_LHV]
| PEM FC CHP PL | 15 | 10.0929 | 53.8% | 36.2% | 90% | [163] | 27.881 | PL | 1_H2 | 1_Heat | 1_EE | 2_H2 | 2_Heat | 2_EE
| PEM FC CHP NL | 75 | 75 | 45% | 45% | 90% | [163] | 166.6667 | NL | 22.3048 | 8.0743 | 12 | 133.3333 | 60 | 60
| PEM FC CHP PL | 15 | 10.0929 | 53.8% | 36.2% | 90% | [163] | 27.881 | PL
| PEM FC CHP NL | 100 | 100 | 45% | 45% | 90% | [163] | 222.2222 | NL
| PEM FC CHP PL | 30 | 20 | 54% | 36% | 90% | [163] | 55.5556 | PL | 1_H2 | 1_Heat | 1_EE | 2_H2 | 2_Heat | 2_EE
| PEM FC CHP NL | 200 | 191.3043 | 46% | 44% | 90% | [163] | 434.7826 | NL | 277.7778 | 100 | 150 | 2173.913 | 956.5217 | 1000
| Ref | Link
[163] | Zero-Emission Power Generation Solutions | https://powercellgroup.com/segments/power-generation/
|  |  |  | EE | HEAT | EE | HEAT | EE | HEAT
| Point | XD (size) [kW_el] | In (input) [kW_LHV] | Out (output) [kW_el] | Out (output) [kW_th] | Out calc (output) [kW_el] | Out calc (output) [kW_th] | Out err | Out err
| PL | 75 | 27.881 | 15 | 10.0929 | 13.8072 | 11.2857 | 7.952% | -11.82%
| NL | 75 | 166.6667 | 75 | 75 | 75.5271 | 74.4729 | -0.7028% | 0.7028%
| PL | 100 | 27.881 | 15 | 10.0929 | 14.7029 | 10.39 | 1.981% | -2.943%
| NL | 100 | 222.2222 | 100 | 100 | 101.1292 | 98.8708 | -1.129% | 1.129%
| PL | 200 | 55.5556 | 30 | 20 | 30.593 | 19.407 | -1.977% | 2.965%
| NL | 200 | 434.7826 | 200 | 191.3043 | 199.2406 | 192.0638 | 0.3797% | -0.397%
| k1 EE | k2 EE | k3 EE |  | k1 HEAT | k2 HEAT | k3 HEAT
| 0.44471 | 0.035828 | -1.279 |  | 0.45529 | -0.035828 | 1.279
| 0.44471 | 0.035828 | -1.279 |  | 0.45529 | -0.035828 | 1.279
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_EE | 1_Heat |  | 2_NG | 2_EE | 2_Heat
| 0.15 | 0.10254 | 0.032465 |  | 1 | 0.48054 | 0.41946
https://ecp.ep.liu.se/index.php/sims/article/download/515/475/437

## Check PEMFC
Output Power [kW_th] | Fuel Cell Stack Performance [MJ/kg_H2] | eff LHV [%] | Input [kW_th] (LHV)
18.75 | 64.3 | 53.58% | 34.9922
31.25 | 63.8 | 53.17% | 58.7774
50 | 62.2 | 51.83% | 96.463
62.5 | 60.8 | 50.67% | 123.3553
75 | 59.5 | 49.58% | 151.2605
93.75 | 57.8 | 48.17% | 194.6367
100 | 57.1 | 47.58% | 210.1576
125 | 56.3 | 46.92% | 266.4298

## Dati_Absorption
| Size [TR] | Size [kW_th] | NG input [Nm³/h] | Heat Input [kW_th] | COP NL | COP PL
| 57 | 200.469 | 13.2 | 129.8497 | 1.5439 | 1.8827
| 69 | 242.673 | 16 | 157.3936 | 1.5418 | 1.8803
| 87 | 305.979 | 19.7 | 193.7909 | 1.5789 | 1.9255
| 104 | 365.768 | 24.2 | 238.0578 | 1.5365 | 1.8737
| 138 | 485.346 | 32.1 | 315.7709 | 1.537 | 1.8744
| 172 | 604.924 | 40.1 | 394.4677 | 1.5335 | 1.8701
| 211 | 742.087 | 48.9 | 481.0342 | 1.5427 | 1.8813
| 249 | 875.733 | 57.7 | 567.6007 | 1.5429 | 1.8815
| 290 | 1019.93 | 67.15 | 660.5613 | 1.544 | 1.883
| 333 | 1171.161 | 77.11 | 758.5388 | 1.544 | 1.8829
| 377 | 1325.909 | 87.2 | 857.7951 | 1.5457 | 1.885
| 425 | 1494.725 | 96.1 | 945.3453 | 1.5811 | 1.9282
| 480 | 1688.16 | 108.25 | 1064.8661 | 1.5853 | 1.9333
| 540 | 1899.18 | 122.1 | 1201.1099 | 1.5812 | 1.9283
| 600 | 2110.2 | 135.7 | 1334.8945 | 1.5808 | 1.9278
| 666 | 2342.322 | 150.6 | 1481.4673 | 1.5811 | 1.9281
| 750 | 2637.75 | 169.6 | 1668.3722 | 1.581 | 1.9281
| 825 | 2901.525 | 186.6 | 1835.6029 | 1.5807 | 1.9277
| 900 | 3165.3 | 203.8 | 2004.801 | 1.5789 | 1.9254
| 1000 | 3517 | 226.7 | 2230.0706 | 1.5771 | 1.9233
| 1100 | 3868.7 | 248.88 | 2448.2574 | 1.5802 | 1.9271
| 1225 | 4308.325 | 277.13 | 2726.1555 | 1.5804 | 1.9273
| 1342 | 4719.814 | 303.8 | 2988.511 | 1.5793 | 1.926
| 1500 | 5275.5 | 339.6 | 3340.6792 | 1.5792 | 1.9258
| 1678 | 5901.526 | 379.9 | 3737.1143 | 1.5792 | 1.9258
| 1820 | 6400.94 | 411.94 | 4052.295 | 1.5796 | 1.9263
| [164] | 1 TR = 3.517 kW_th | NCVgas= 9000 kcal/Nm3 = 10.465 kWh/Nm3 |  | [164] | FCRp =0.82 | [166]
|  |  | eff_burner = 0.94 |  | [165]
| Reference | Link
[164] | Direct Fired VAM XP Series | https://www.thermaxglobal.com/wp-content/uploads/2024/09/Direct-Fired-Absorption-Chiller-XP-Brochure.pdf
[165] | RTC 3000-4000-5000-6000 RTC 8000-10000 | https://www.mechanicalresource.com/hubfs/Resource%20Center%20Files/White%20Papers/Riello/RTC%203000-4000-5000-6000%20RTC%208000-10000%20RTC%20USA%20INSTALLATION%2C%20OPERATION%20AND%20SERVICE%20MANUAL.pdf?hsLang=en
valido su tutta gamma
[166] | https://www.shareddocs.com/hvac/docs/1001/Public/0E/16DNH-Product-data-PD5-20090423.pdf

## ABSORPTION Chill steam
| Absorption Chiller steam | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_th]
| absorption chiller large PL | 50.1172 | 1.8829 | [166] | 26.6167 | PL
| absorption chiller large NL | 200.469 | 1.544 | [164] | 129.8374 | NL
| absorption chiller large PL | 60.6683 | 1.8805 | [166] | 32.262 | PL
| absorption chiller large NL | 242.673 | 1.542 | [164] | 157.3755 | NL
| absorption chiller large PL | 76.4947 | 1.9256 | [166] | 39.7249 | PL
| absorption chiller large NL | 305.979 | 1.579 | [164] | 193.7802 | NL
| absorption chiller large PL | 91.442 | 1.8732 | [166] | 48.8167 | PL
| absorption chiller large NL | 365.768 | 1.536 | [164] | 238.1302 | NL
| absorption chiller large PL | 121.3365 | 1.8744 | [166] | 64.7339 | PL
| absorption chiller large NL | 485.346 | 1.537 | [164] | 315.7749 | NL
| absorption chiller large PL | 151.231 | 1.8707 | [166] | 80.8406 | PL
| absorption chiller large NL | 604.924 | 1.534 | [164] | 394.3442 | NL
| absorption chiller large PL | 185.5217 | 1.8817 | [166] | 98.5922 | PL
| absorption chiller large NL | 742.087 | 1.543 | [164] | 480.9378 | NL
| absorption chiller large PL | 218.9332 | 1.8817 | [166] | 116.3482 | PL
| absorption chiller large NL | 875.733 | 1.543 | [164] | 567.5522 | NL
| absorption chiller large PL | 254.9825 | 1.8829 | [166] | 135.4182 | PL
| absorption chiller large NL | 1019.93 | 1.544 | [164] | 660.5764 | NL
| absorption chiller large PL | 292.7903 | 1.8829 | [166] | 155.4974 | PL | 1_EE_input | 1_Cooling | 2_EE_input | 2_Cooling
| absorption chiller large NL | 1171.161 | 1.544 | [164] | 758.524 | NL | 154.1483 | 290.25 | 751.943 | 1161
| absorption chiller large PL | 331.4772 | 1.8854 | [166] | 175.8159 | PL
| absorption chiller large NL | 1325.909 | 1.546 | [164] | 857.6384 | NL
| absorption chiller large PL | 373.6812 | 1.928 | [166] | 193.8132 | PL
| absorption chiller large NL | 1494.725 | 1.581 | [164] | 945.4301 | NL
| absorption chiller large PL | 422.04 | 1.9329 | [166] | 218.3425 | PL
| absorption chiller large NL | 1688.16 | 1.585 | [164] | 1065.0852 | NL
| absorption chiller large PL | 474.795 | 1.928 | [166] | 246.2567 | PL
| absorption chiller large NL | 1899.18 | 1.581 | [164] | 1201.2524 | NL
| absorption chiller large PL | 527.55 | 1.928 | [166] | 273.6186 | PL
| absorption chiller large NL | 2110.2 | 1.581 | [164] | 1334.7249 | NL
| absorption chiller large PL | 585.5805 | 1.928 | [166] | 303.7166 | PL
| absorption chiller large NL | 2342.322 | 1.581 | [164] | 1481.5446 | NL
| absorption chiller large PL | 659.4375 | 1.928 | [166] | 342.0232 | PL
| absorption chiller large NL | 2637.75 | 1.581 | [164] | 1668.4061 | NL
| absorption chiller large PL | 725.3813 | 1.928 | [166] | 376.2256 | PL
| absorption chiller large NL | 2901.525 | 1.581 | [164] | 1835.2467 | NL
| absorption chiller large PL | 791.325 | 1.9256 | [166] | 410.9478 | PL
| absorption chiller large NL | 3165.3 | 1.579 | [164] | 2004.6232 | NL
| absorption chiller large PL | 879.25 | 1.9232 | [166] | 457.1877 | PL
| absorption chiller large NL | 3517 | 1.577 | [164] | 2230.1839 | NL
| absorption chiller large PL | 967.175 | 1.9268 | [166] | 501.9516 | PL
| absorption chiller large NL | 3868.7 | 1.58 | [164] | 2448.5443 | NL
| absorption chiller large PL | 1077.0812 | 1.9268 | [166] | 558.9915 | PL
| absorption chiller large NL | 4308.325 | 1.58 | [164] | 2726.788 | NL
| absorption chiller large PL | 1179.9535 | 1.9256 | [166] | 612.7688 | PL | 1_H_input | 1_Cooling | 2_H_input | 2_Cooling
| absorption chiller large NL | 4719.814 | 1.579 | [164] | 2989.1159 | NL | 602.6662 | 1160.5 | 2939.8353 | 4642
| absorption chiller large PL | 1318.875 | 1.9256 | [166] | 684.9129 | PL
| absorption chiller large NL | 5275.5 | 1.579 | [164] | 3341.0386 | NL
| absorption chiller large PL | 1475.3815 | 1.9256 | [166] | 766.1893 | PL
| absorption chiller large NL | 5901.526 | 1.579 | [164] | 3737.5085 | NL
| absorption chiller large PL | 1600.235 | 1.9268 | [166] | 830.5017 | PL
| absorption chiller large NL | 6400.94 | 1.58 | [164] | 4051.2278 | NL
| Ref | Link
[164] | Direct Fired VAM XP Series | https://www.thermaxglobal.com/wp-content/uploads/2024/09/Direct-Fired-Absorption-Chiller-XP-Brochure.pdf
[166] | 16DNH - Product Data | https://www.shareddocs.com/hvac/docs/1001/Public/0E/16DNH-Product-data-PD5-20090423.pdf
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 200.469 | 26.6167 | 50.1172 | 44.4518 | 11.3%
| NL | 200.469 | 129.8374 | 200.469 | 198.1614 | 1.151%
| PL | 242.673 | 32.262 | 60.6682 | 55.3263 | 8.805%
| NL | 242.673 | 157.3755 | 242.673 | 241.6372 | 0.4268%
| PL | 305.979 | 39.7249 | 76.4947 | 70.1416 | 8.305%
| NL | 305.979 | 193.7802 | 305.979 | 299.5507 | 2.101%
| PL | 365.768 | 48.8167 | 91.442 | 87.1766 | 4.665%
| NL | 365.768 | 238.1302 | 365.768 | 369.09 | -0.9082%
| PL | 485.346 | 64.7339 | 121.3365 | 117.8719 | 2.855%
| NL | 485.346 | 315.7749 | 485.346 | 491.7059 | -1.31%
| PL | 604.924 | 80.8406 | 151.231 | 148.8494 | 1.575%
| NL | 604.924 | 394.3442 | 604.924 | 615.6987 | -1.781%
| PL | 742.087 | 98.5922 | 185.5217 | 183.3048 | 1.195%
| NL | 742.087 | 480.9378 | 742.087 | 752.669 | -1.426%
| PL | 875.733 | 116.3482 | 218.9332 | 217.5609 | 0.6268%
| NL | 875.733 | 567.5522 | 875.733 | 889.4647 | -1.568%
| PL | 1019.93 | 135.4182 | 254.9825 | 254.3908 | 0.2321%
| NL | 1019.93 | 660.5764 | 1019.93 | 1036.4224 | -1.617%
| PL | 1171.161 | 155.4974 | 292.7903 | 293.1349 | -0.1177%
| NL | 1171.161 | 758.524 | 1171.161 | 1191.123 | -1.704%
| PL | 1325.909 | 175.8159 | 331.4772 | 332.4409 | -0.2907%
| NL | 1325.909 | 857.6384 | 1325.909 | 1347.7668 | -1.649%
| PL | 1494.725 | 193.8132 | 373.6812 | 369.113 | 1.223%
| NL | 1494.725 | 945.4301 | 1494.725 | 1488.3722 | 0.425%
| PL | 1688.16 | 218.3425 | 422.04 | 416.9517 | 1.206%
| NL | 1688.16 | 1065.0852 | 1688.16 | 1677.8661 | 0.6098%
| PL | 1899.18 | 246.2567 | 474.795 | 470.8595 | 0.8289%
| NL | 1899.18 | 1201.2524 | 1899.18 | 1892.9771 | 0.3266%
| PL | 2110.2 | 273.6186 | 527.55 | 523.9446 | 0.6834%
| NL | 2110.2 | 1334.7249 | 2110.2 | 2104.0753 | 0.2902%
| PL | 2342.322 | 303.7166 | 585.5805 | 582.3383 | 0.5537%
| NL | 2342.322 | 1481.5446 | 2342.322 | 2336.2834 | 0.2578%
| PL | 2637.75 | 342.0232 | 659.4375 | 656.6574 | 0.4216%
| NL | 2637.75 | 1668.4061 | 2637.75 | 2631.8208 | 0.2248%
| PL | 2901.525 | 376.2256 | 725.3813 | 723.0139 | 0.3264%
| NL | 2901.525 | 1835.2467 | 2901.525 | 2895.6936 | 0.201%
| PL | 3165.3 | 410.9478 | 791.325 | 790.1444 | 0.1492%
| NL | 3165.3 | 2004.6232 | 3165.3 | 3163.3426 | 0.06184%
| PL | 3517 | 457.1877 | 879.25 | 879.568 | -0.03617%
| NL | 3517 | 2230.1839 | 3517 | 3519.7991 | -0.07959%
| PL | 3868.7 | 501.9516 | 967.175 | 966.7935 | 0.03944%
| NL | 3868.7 | 2448.5443 | 3868.7 | 3865.5333 | 0.08185%
| PL | 4308.325 | 558.9915 | 1077.0812 | 1077.4413 | -0.03342%
| NL | 4308.325 | 2726.788 | 4308.325 | 4305.5833 | 0.06364%
| PL | 4719.814 | 612.7688 | 1179.9535 | 1181.5851 | -0.1383%
| NL | 4719.814 | 2989.1159 | 4719.814 | 4720.2873 | -0.01003%
| PL | 5275.5 | 684.9129 | 1318.875 | 1321.5118 | -0.1999%
| NL | 5275.5 | 3341.0386 | 5275.5 | 5276.8422 | -0.02544%
| PL | 5901.526 | 766.1893 | 1475.3815 | 1479.1508 | -0.2555%
| NL | 5901.526 | 3737.5085 | 5901.526 | 5903.8471 | -0.03933%
| PL | 6400.94 | 830.5017 | 1600.235 | 1604.1246 | -0.2431%
| NL | 6400.94 | 4051.2278 | 6400.94 | 6400.2213 | 0.01123%
| k1 | k2 | k3
| 1.4891 | 0.058476 | -6.9067
| 1.4891 | 0.058476 | -6.9067
| L_min | 25%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_Heat_input | 1_Heat |  |  | 2_Heat_input | 2_Heat
| 0.25 | 0.43076 |  |  | 1 | 1.5476

## ABSORPTION Chill hot water
| Absorption Chiller hot water | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_th]
| absorption chiller large PL | 175.8 | 0.879 | [167][168] | 200 | PL
| absorption chiller large NL | 351.6 | 0.7325 | [167] | 480 | NL
| absorption chiller large PL | 500 | 0.936 | [167][168] | 534.188 | PL | 1_H_input | 1_Cooling | 2_H_input | 2_Cooling
| absorption chiller large NL | 1000 | 0.78 | [167] | 1282.0513 | NL | 534.188 | 500 | 1282.0513 | 1000
| absorption chiller large PL | 3100 | 0.972 | [167][168] | 3189.3004 | PL
| absorption chiller large NL | 6200 | 0.81 | [167] | 7654.321 | NL
| Ref | Link
[167] | GRUPPI REFRIGERANTI ALIMENTATI AD ACQUA CALDA 1 Specifiche tecniche - Yazaki | https://maya-airconditioning.com/wp-content/uploads/2022/10/1_WFC_MBCE1_Specifiche_tecniche_ver_1_22.pdf
[168] | PRODUCT CATALOGUE FOR ABSORPTION MACHINES Chillers and Heat pumps | https://documentos.mollier.pt/thermax/catalogue2024_tac_l1_eng.pdf
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 351.6 | 200 | 175.8 | 165.0231 | 6.13%
| NL | 351.6 | 480 | 351.6 | 359.156 | -2.149%
| PL | 1000 | 534.188 | 500 | 492.5526 | 1.489%
| NL | 1000 | 1282.0513 | 1000 | 1011.07 | -1.107%
| PL | 6200 | 3189.3004 | 3100 | 3101.9286 | -0.06221%
| NL | 6200 | 7654.321 | 6200 | 6197.6698 | 0.03758%
| k1 | k2 | k3
| 0.69333 | 0.14779 | -25.6059
| 0.69333 | 0.14779 | -25.6059
| L_min | 50%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_Heat_input | 1_Heat |  |  | 2_Heat_input | 2_Heat
| 0.5 | 0.49445 |  |  | 1 | 0.84112

## Check ABS chill
STEAM |  | PL | FCRp
| absorption chiller large PL | 25% | 0.82
| absorption chiller large PL | 30% | 0.825
| absorption chiller large PL | 40% | 0.85
| absorption chiller large PL | 50% | 0.885
| absorption chiller large PL | 60% | 0.93
| absorption chiller large PL | 70% | 0.97
| absorption chiller large PL | 80% | 0.99
| absorption chiller large PL | 90% | 0.998
| absorption chiller large NL | 100% | 1
| Model 1820 TR | PL | FCRp | Output [kW_th] | COPp | Input [kW_th]
| absorption chiller large PL | 25% | 0.82 | 1600.235 | 1.9268 | 830.5017
| absorption chiller large PL | 30% | 0.825 | 1920.282 | 1.9152 | 1002.6789
| absorption chiller large PL | 40% | 0.85 | 2560.376 | 1.8588 | 1377.4175
| absorption chiller large PL | 50% | 0.885 | 3200.47 | 1.7853 | 1792.6683
| absorption chiller large PL | 60% | 0.93 | 3840.564 | 1.6989 | 2260.5851
| absorption chiller large PL | 70% | 0.97 | 4480.658 | 1.6289 | 2750.7837
| absorption chiller large PL | 80% | 0.99 | 5120.752 | 1.596 | 3208.5725
| absorption chiller large PL | 90% | 0.998 | 5760.846 | 1.5832 | 3638.8129
| absorption chiller large NL | 100% | 1 | 6400.94 | 1.58 | 4051.2278
HOT WATER
| % Acqua IN | Out | In | Coeff pen | COP | COP_pl/COP_nl
| 100% | 351.6 | 480 | 1 | 0.7325 | 1
| 90% | 329.3789 | 432 | 0.9368 | 0.76245 | 1.0409
| 80% | 304.7317 | 384 | 0.8667 | 0.79357 | 1.0834
| 70% | 281.28 | 336 | 0.8 | 0.83714 | 1.1429
| 60% | 241.7953 | 288 | 0.6877 | 0.83957 | 1.1462
| 50% | 210.96 | 240 | 0.6 | 0.879 | 1.2

## Trane_W_COMPRESSION_Small
| Compression Chiller (water) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| Compression chiller large PL | 11.1 | 8.96 | [177] | 1.2388 | PL
| Compression chiller large NL | 52.7 | 5.04 | [177] | 10.4563 | NL
| Compression chiller large PL | 12.7 | 8.75 | [177] | 1.4514 | PL
| Compression chiller large NL | 60.4 | 4.92 | [177] | 12.2764 | NL
| Compression chiller large PL | 14.7 | 8.83 | [177] | 1.6648 | PL
| Compression chiller large NL | 69.7 | 5.03 | [177] | 13.8569 | NL
| Compression chiller large PL | 17.6 | 8.88 | [177] | 1.982 | PL
| Compression chiller large NL | 83.6 | 5.04 | [177] | 16.5873 | NL
| Compression chiller large PL | 19.8 | 8.14 | [177] | 2.4324 | PL
| Compression chiller large NL | 94 | 5 | [177] | 18.8 | NL
| Compression chiller large PL | 23.4 | 8.24 | [177] | 2.8398 | PL
| Compression chiller large NL | 111.2 | 5.04 | [177] | 22.0635 | NL
| Compression chiller large PL | 27.4 | 8.71 | [177] | 3.1458 | PL
| Compression chiller large NL | 129.8 | 5.17 | [177] | 25.1064 | NL
| Compression chiller large PL | 30.1 | 8.62 | [177] | 3.4919 | PL
| Compression chiller large NL | 143.1 | 5.11 | [177] | 28.0039 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  |  | Note: models CGWF HE R454B
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 52.7 | 1.2388 | 11.1 | 11.4703 | -3.336%
| NL | 52.7 | 10.4563 | 52.7 | 53.6439 | -1.791%
| PL | 60.4 | 1.4514 | 12.7 | 13.2907 | -4.651%
| NL | 60.4 | 12.2764 | 60.4 | 62.8192 | -4.005%
| PL | 69.7 | 1.6648 | 14.7 | 15.2908 | -4.019%
| NL | 69.7 | 13.8569 | 69.7 | 71.0742 | -1.972%
| PL | 83.6 | 1.982 | 17.6 | 18.2725 | -3.821%
| NL | 83.6 | 16.5873 | 83.6 | 85.0974 | -1.791%
| PL | 94 | 2.4324 | 19.8 | 21.4785 | -8.477%
| NL | 94 | 18.8 | 94 | 96.3663 | -2.517%
| PL | 111.2 | 2.8398 | 23.4 | 25.2361 | -7.846%
| NL | 111.2 | 22.0635 | 111.2 | 113.1917 | -1.791%
| PL | 129.8 | 3.1458 | 27.4 | 28.684 | -4.686%
| NL | 129.8 | 25.1064 | 129.8 | 129.1619 | 0.4916%
| PL | 143.1 | 3.4919 | 30.1 | 31.7317 | -5.421%
| NL | 143.1 | 28.0039 | 143.1 | 143.8836 | -0.5476%
| k1 | k2 | k3
| 4.5754 | 0.1101 | -1.2121
| 4.5754 | 0.1101 | -1.2121
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_EE_input | 1_Cooling |  |  | 2_EE_input | 2_Cooling
| 0.2 | 1.0252 |  |  | 1 | 4.6855

## Trane_W_COMPRESSION_Mid
| Compression Chiller (water) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| Compression chiller large PL | 32.8 | 8.12 | [177] | 4.0394 | PL
| Compression chiller large NL | 155.8 | 5.01 | [177] | 31.0978 | NL
| Compression chiller large PL | 33.3 | 7.9 | [177] | 4.2152 | PL
| Compression chiller large NL | 158 | 5.04 | [177] | 31.3492 | NL
| Compression chiller large PL | 39 | 7.56 | [177] | 5.1587 | PL
| Compression chiller large NL | 185 | 4.96 | [177] | 37.2984 | NL
| Compression chiller large PL | 45.7 | 7.62 | [177] | 5.9974 | PL
| Compression chiller large NL | 217.2 | 4.87 | [177] | 44.5996 | NL
| Compression chiller large PL | 52.7 | 7.83 | [177] | 6.7305 | PL
| Compression chiller large NL | 250.4 | 4.93 | [177] | 50.7911 | NL
| Compression chiller large PL | 58.5 | 8.01 | [177] | 7.3034 | PL
| Compression chiller large NL | 277.7 | 5.04 | [177] | 55.0992 | NL
| Compression chiller large PL | 63.7 | 7.82 | [177] | 8.1458 | PL
| Compression chiller large NL | 302.7 | 4.99 | [177] | 60.6613 | NL
| Compression chiller large PL | 69.8 | 7.52 | [177] | 9.2819 | PL
| Compression chiller large NL | 331.4 | 4.77 | [177] | 69.4759 | NL
| Compression chiller large PL | 78.4 | 7.98 | [177] | 9.8246 | PL
| Compression chiller large NL | 372.2 | 4.88 | [177] | 76.2705 | NL
| Compression chiller large PL | 90.8 | 7.87 | [177] | 11.5375 | PL
| Compression chiller large NL | 431.1 | 4.97 | [177] | 86.7404 | NL
| Compression chiller large PL | 101.9 | 8.62 | [177] | 11.8213 | PL
| Compression chiller large NL | 483.7 | 5.02 | [177] | 96.3546 | NL
| Compression chiller large PL | 118.7 | 7.84 | [177] | 15.1403 | PL
| Compression chiller large NL | 563.5 | 4.9 | [177] | 115 | NL
| Compression chiller large PL | 129.4 | 7.94 | [177] | 16.2972 | PL
| Compression chiller large NL | 614.2 | 4.87 | [177] | 126.1191 | NL
| Compression chiller large PL | 139.8 | 8.06 | [177] | 17.3449 | PL
| Compression chiller large NL | 663.8 | 4.83 | [177] | 137.4327 | NL
| Compression chiller large PL | 146.3 | 7.77 | [177] | 18.8288 | PL
| Compression chiller large NL | 694.8 | 4.67 | [177] | 148.7794 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  |  | Note: models CGWF HE R454B
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 155.8 | 4.0394 | 32.8 | 30.8618 | 5.909%
| NL | 155.8 | 31.0978 | 155.8 | 149.8579 | 3.814%
| PL | 158 | 4.2152 | 33.3 | 31.8198 | 4.445%
| NL | 158 | 31.3492 | 158 | 151.1485 | 4.336%
| PL | 185 | 5.1587 | 39 | 38.2391 | 1.951%
| NL | 185 | 37.2984 | 185 | 179.5813 | 2.929%
| PL | 217.2 | 5.9974 | 45.7 | 44.6341 | 2.332%
| NL | 217.2 | 44.5996 | 217.2 | 214.3971 | 1.29%
| PL | 250.4 | 6.7305 | 52.7 | 50.6493 | 3.891%
| NL | 250.4 | 50.7911 | 250.4 | 244.4167 | 2.39%
| PL | 277.7 | 7.3034 | 58.5 | 55.4636 | 5.19%
| NL | 277.7 | 55.0992 | 277.7 | 265.6578 | 4.336%
| PL | 302.7 | 8.1458 | 63.7 | 61.2699 | 3.815%
| NL | 302.7 | 60.6613 | 302.7 | 292.2202 | 3.462%
| PL | 331.4 | 9.2819 | 69.8 | 68.6791 | 1.606%
| NL | 331.4 | 69.4759 | 331.4 | 333.3972 | -0.6027%
| PL | 372.2 | 9.8246 | 78.4 | 74.4954 | 4.98%
| NL | 372.2 | 76.2705 | 372.2 | 366.7081 | 1.476%
| PL | 431.1 | 11.5375 | 90.8 | 86.9799 | 4.207%
| NL | 431.1 | 86.7404 | 431.1 | 417.7038 | 3.107%
| PL | 483.7 | 11.8213 | 101.9 | 92.6501 | 9.077%
| NL | 483.7 | 96.3546 | 483.7 | 464.4063 | 3.989%
| PL | 563.5 | 15.1403 | 118.7 | 113.9546 | 3.998%
| NL | 563.5 | 115 | 563.5 | 553.1127 | 1.843%
| PL | 614.2 | 16.2972 | 129.4 | 123.3046 | 4.711%
| NL | 614.2 | 126.1191 | 614.2 | 606.2738 | 1.29%
| PL | 663.8 | 17.3449 | 139.8 | 132.0817 | 5.521%
| NL | 663.8 | 137.4327 | 663.8 | 660.198 | 0.5426%
| PL | 694.8 | 18.8288 | 146.3 | 141.2137 | 3.477%
| NL | 694.8 | 148.7794 | 694.8 | 712.7041 | -2.577%
| k1 | k2 | k3
| 4.3978 | 0.084066 | 4.8073
| 4.3978 | 0.084066 | 4.8073
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_EE_input | 1_Cooling |  |  | 2_EE_input | 2_Cooling
| 0.2 | 0.96362 |  |  | 1 | 4.4818

## Check Trane_W_Compr_Chill Sm-Mi
Model 52.7 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
52.7 | 5.04 | 10.4563
38.8 | 6.31 | 6.149
25 | 7.84 | 3.1888
11.1 | 8.96 | 1.2388
Model 217.2 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
217.2 | 4.87 | 44.5996
160 | 5.91 | 27.0728
102.9 | 6.9 | 14.913
45.7 | 7.62 | 5.9974
Model 694.8 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
694.8 | 4.67 | 148.7794
512.2 | 6.07 | 84.3822
329.2 | 7.43 | 44.3069
146.3 | 7.77 | 18.8288

## Trane_W_COMPRESSION_Big_C
| Compression Chiller (water) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| Compression chiller large PL | 178.3 | 8 | [177] | 22.2875 | PL
| Compression chiller large NL | 849 | 5.76 | [177] | 147.3958 | NL
| Compression chiller large PL | 196.6 | 8 | [177] | 24.575 | PL
| Compression chiller large NL | 936.1 | 5.66 | [177] | 165.3887 | NL
| Compression chiller large PL | 225.9 | 8.08 | [177] | 27.9579 | PL | 1_EE_input | 1_Cooling | 2_EE_input | 2_Cooling
| Compression chiller large NL | 1075.9 | 5.52 | [177] | 194.9094 | NL | 25.9856 | 209.9638 | 181.1594 | 1000
| Compression chiller large PL | 242.7 | 8.1 | [177] | 29.963 | PL
| Compression chiller large NL | 1155.7 | 5.44 | [177] | 212.4449 | NL
| Compression chiller large PL | 272 | 7.55 | [177] | 36.0265 | PL
| Compression chiller large NL | 1295.2 | 5.38 | [177] | 240.7435 | NL
| Compression chiller large PL | 289.8 | 7.62 | [177] | 38.0315 | PL
| Compression chiller large NL | 1379.8 | 5.36 | [177] | 257.4254 | NL
| Compression chiller large PL | 330 | 7.87 | [177] | 41.9314 | PL
| Compression chiller large NL | 1571.2 | 6.14 | [177] | 255.8958 | NL
| Compression chiller large PL | 351.7 | 7.96 | [177] | 44.1834 | PL
| Compression chiller large NL | 1674.9 | 5.96 | [177] | 281.0235 | NL
| Compression chiller large PL | 392.1 | 8.01 | [177] | 48.9513 | PL
| Compression chiller large NL | 1867.4 | 6.1 | [177] | 306.1311 | NL
| Compression chiller large PL | 408.6 | 7.66 | [177] | 53.342 | PL
| Compression chiller large NL | 1945.9 | 5.92 | [177] | 328.6993 | NL
| Compression chiller large PL | 430.5 | 7.72 | [177] | 55.7642 | PL
| Compression chiller large NL | 2049.9 | 5.72 | [177] | 358.3741 | NL
| Compression chiller large PL | 452.6 | 7.49 | [177] | 60.4272 | PL
| Compression chiller large NL | 2155.2 | 5.57 | [177] | 386.93 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  |  | Note: Chosen models with XE Low Vi E...B C...C1 R1234ze
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 849 | 22.2875 | 178.3 | 193.4941 | -8.522%
| NL | 849 | 147.3958 | 849 | 862.7712 | -1.622%
| PL | 936.1 | 24.575 | 196.6 | 213.3502 | -8.52%
| NL | 936.1 | 165.3887 | 936.1 | 966.6444 | -3.263%
| PL | 1075.9 | 27.9579 | 225.9 | 243.6763 | -7.869%
| NL | 1075.9 | 194.9094 | 1075.9 | 1136.7968 | -5.66%
| PL | 1155.7 | 29.963 | 242.7 | 261.3828 | -7.698%
| NL | 1155.7 | 212.4449 | 1155.7 | 1237.5844 | -7.085%
| PL | 1295.2 | 36.0265 | 272 | 306.0228 | -12.51%
| NL | 1295.2 | 240.7435 | 1295.2 | 1401.1729 | -8.182%
| PL | 1379.8 | 38.0315 | 289.8 | 324.149 | -11.85%
| NL | 1379.8 | 257.4254 | 1379.8 | 1497.8142 | -8.553%
| PL | 1571.2 | 41.9314 | 330 | 361.7543 | -9.623%
| NL | 1571.2 | 255.8958 | 1571.2 | 1506.374 | 4.126%
| PL | 1674.9 | 44.1834 | 351.7 | 382.8727 | -8.863%
| NL | 1674.9 | 281.0235 | 1674.9 | 1649.8678 | 1.495%
| PL | 1867.4 | 48.9513 | 392.1 | 425.2177 | -8.446%
| NL | 1867.4 | 306.1311 | 1867.4 | 1801.022 | 3.555%
| PL | 1945.9 | 53.342 | 408.6 | 455.5729 | -11.5%
| NL | 1945.9 | 328.6993 | 1945.9 | 1928.619 | 0.8881%
| PL | 2049.9 | 55.7642 | 430.5 | 477.628 | -10.95%
| NL | 2049.9 | 358.3741 | 2049.9 | 2096.464 | -2.272%
| PL | 2155.2 | 60.4272 | 452.6 | 511.7841 | -13.08%
| NL | 2155.2 | 386.93 | 2155.2 | 2258.4368 | -4.79%
| k1 | k2 | k3
| 5.3496 | 0.087474 | -32.228
| 5.3496 | 0.087474 | -32.228
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_EE_input | 1_Cooling |  |  | 2_EE_input | 2_Cooling
| 0.2 | 1.1574 |  |  | 1 | 5.4371

## Check Trane_W_Compr_Chill B
Model 849 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
849 | 5.76 | 147.3958
628.3 | 6.77 | 92.8065
399.1 | 7.86 | 50.7761
178.3 | 8 | 22.2875
Model 1571.2 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
1571.2 | 6.14 | 255.8958
1162.7 | 7.01 | 165.8631
738.5 | 8.48 | 87.0873
330 | 7.87 | 41.9314
Model 2155.2 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
2155.2 | 5.57 | 386.93
1594.9 | 6.42 | 248.4268
1013 | 7.33 | 138.1992
452.6 | 7.49 | 60.4272

## Trane_A_COMPRESSION_Smal
| Compression Chiller (air) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| Compression chiller large PL | 8.6 | 4.81 | [177] | 1.7879 | PL
| Compression chiller large NL | 40.7 | 2.8 | [177] | 14.5357 | NL
| Compression chiller large PL | 10.1 | 5.22 | [177] | 1.9349 | PL
| Compression chiller large NL | 48.1 | 2.79 | [177] | 17.2401 | NL
| Compression chiller large PL | 11.8 | 4.89 | [177] | 2.4131 | PL
| Compression chiller large NL | 56.1 | 3.12 | [177] | 17.9808 | NL
| Compression chiller large PL | 13.3 | 5.05 | [177] | 2.6337 | PL
| Compression chiller large NL | 63.3 | 3.02 | [177] | 20.9603 | NL
| Compression chiller large PL | 15.6 | 4.92 | [177] | 3.1707 | PL
| Compression chiller large NL | 74.2 | 3.05 | [177] | 24.3279 | NL
| Compression chiller large PL | 17.1 | 4.68 | [177] | 3.6538 | PL
| Compression chiller large NL | 81.3 | 2.92 | [177] | 27.8425 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  |  | Note: models CGAX HE LN R454B
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 40.7 | 1.7879 | 8.6 | 9.7064 | -12.86%
| NL | 40.7 | 14.5357 | 40.7 | 43.8755 | -7.802%
| PL | 48.1 | 1.9349 | 10.1 | 10.9936 | -8.848%
| NL | 48.1 | 17.2401 | 48.1 | 52.018 | -8.145%
| PL | 56.1 | 2.4131 | 11.8 | 13.2414 | -12.21%
| NL | 56.1 | 17.9808 | 56.1 | 54.969 | 2.016%
| PL | 63.3 | 2.6337 | 13.3 | 14.7019 | -10.54%
| NL | 63.3 | 20.9603 | 63.3 | 63.8246 | -0.8287%
| PL | 74.2 | 3.1707 | 15.6 | 17.4575 | -11.91%
| NL | 74.2 | 24.3279 | 74.2 | 74.1671 | 0.04428%
| PL | 81.3 | 3.6538 | 17.1 | 19.6096 | -14.68%
| NL | 81.3 | 27.8425 | 81.3 | 84.4449 | -3.868%
| k1 | k2 | k3
| 2.6804 | 0.12074 | -1.5675
| 2.6804 | 0.12074 | -1.5675
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_EE_input | 1_Cooling |  |  | 2_EE_input | 2_Cooling
| 0.2 | 0.65682 |  |  | 1 | 2.8011

## Check Trane_A_Comp_Chill Small
Model 40 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
40.7 | 2.8 | 14.5357
30 | 3.7 | 8.1081
19.3 | 4.6 | 4.1957
8.6 | 4.81 | 1.7879
Model 63 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
63.3 | 3.02 | 20.9603
46.7 | 3.86 | 12.0984
30 | 4.8 | 6.25
13.3 | 5.05 | 2.6337
Model 81 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
81.3 | 2.92 | 27.8425
59.9 | 3.8 | 15.7632
38.5 | 4.61 | 8.3514
17.1 | 4.68 | 3.6538

## Trane_A_COMPRESSION_Mid v2
| Compression Chiller (air) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| Compression chiller large PL | 20.3 | 5.94 | [177] | 3.4175 | PL
| Compression chiller large NL | 96.2 | 2.91 | [177] | 33.0584 | NL
| Compression chiller large PL | 21.1 | 6.29 | [177] | 3.3545 | PL
| Compression chiller large NL | 100 | 3 | [177] | 33.3333 | NL
| Compression chiller large PL | 23.4 | 5.85 | [177] | 4 | PL
| Compression chiller large NL | 111.2 | 3.17 | [177] | 35.0789 | NL
| Compression chiller large PL | 24.4 | 5.83 | [177] | 4.1852 | PL
| Compression chiller large NL | 115.8 | 3.22 | [177] | 35.9627 | NL
| Compression chiller large PL | 25.7 | 5.6 | [177] | 4.5893 | PL
| Compression chiller large NL | 122.1 | 3.05 | [177] | 40.0328 | NL
| Compression chiller large PL | 27.6 | 5.94 | [177] | 4.6465 | PL
| Compression chiller large NL | 130.9 | 3.1 | [177] | 42.2258 | NL
| Compression chiller large PL | 28.9 | 6.28 | [177] | 4.6019 | PL
| Compression chiller large NL | 137 | 3.15 | [177] | 43.4921 | NL
| Compression chiller large PL | 33 | 5.8 | [177] | 5.6897 | PL
| Compression chiller large NL | 156.8 | 2.92 | [177] | 53.6986 | NL
| Compression chiller large PL | 39 | 6.29 | [177] | 6.2003 | PL
| Compression chiller large NL | 185.2 | 3.36 | [177] | 55.119 | NL
| Compression chiller large PL | 41.8 | 6.34 | [177] | 6.5931 | PL
| Compression chiller large NL | 198.6 | 3.31 | [177] | 60 | NL
| Compression chiller large PL | 47.1 | 5.96 | [177] | 7.9027 | PL
| Compression chiller large NL | 223.7 | 3.15 | [177] | 71.0159 | NL
| Compression chiller large PL | 49.8 | 6.01 | [177] | 8.2862 | PL
| Compression chiller large NL | 236.7 | 3.14 | [177] | 75.3822 | NL
| Compression chiller large PL | 52 | 6.05 | [177] | 8.595 | PL
| Compression chiller large NL | 246.8 | 3.09 | [177] | 79.8706 | NL
| Compression chiller large PL | 56.1 | 5.77 | [177] | 9.7227 | PL
| Compression chiller large NL | 266.4 | 2.98 | [177] | 89.396 | NL
| Compression chiller large PL | 65.2 | 6.52 | [177] | 10 | PL
| Compression chiller large NL | 309.7 | 3.36 | [177] | 92.1726 | NL
| Ref | Link |  |  |  |  | Note: models CGAX HE LN R454B till 130 KW
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  |  | Note: models CGAF HE EC LN
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 96.2 | 3.4175 | 20.3 | 22.4397 | -10.54%
| NL | 96.2 | 33.0584 | 96.2 | 104.9281 | -9.073%
| PL | 100 | 3.3545 | 21.1 | 22.7752 | -7.939%
| NL | 100 | 33.3333 | 100 | 106.2039 | -6.204%
| PL | 111.2 | 4 | 23.4 | 26.0767 | -11.44%
| NL | 111.2 | 35.0789 | 111.2 | 112.5668 | -1.229%
| PL | 115.8 | 4.1852 | 24.4 | 27.2105 | -11.52%
| NL | 115.8 | 35.9627 | 115.8 | 115.6448 | 0.134%
| PL | 122.1 | 4.5893 | 25.7 | 29.1816 | -13.55%
| NL | 122.1 | 40.0328 | 122.1 | 127.8181 | -4.683%
| PL | 130.9 | 4.6465 | 27.6 | 30.5234 | -10.59%
| NL | 130.9 | 42.2258 | 130.9 | 135.1038 | -3.211%
| PL | 137 | 4.6019 | 28.9 | 31.2192 | -8.025%
| NL | 137 | 43.4921 | 137 | 139.4476 | -1.787%
| PL | 156.8 | 5.6897 | 33 | 36.9074 | -11.84%
| NL | 156.8 | 53.6986 | 156.8 | 170.5127 | -8.745%
| PL | 185.2 | 6.2003 | 39 | 42.1454 | -8.065%
| NL | 185.2 | 55.119 | 185.2 | 178.2825 | 3.735%
| PL | 198.6 | 6.5931 | 41.8 | 45.0393 | -7.75%
| NL | 198.6 | 60 | 198.6 | 193.6668 | 2.484%
| PL | 223.7 | 7.9027 | 47.1 | 52.0573 | -10.53%
| NL | 223.7 | 71.0159 | 223.7 | 227.6965 | -1.787%
| PL | 236.7 | 8.2862 | 49.8 | 54.8717 | -10.18%
| NL | 236.7 | 75.3822 | 236.7 | 241.5947 | -2.068%
| PL | 246.8 | 8.595 | 52 | 57.0887 | -9.786%
| NL | 246.8 | 79.8706 | 246.8 | 255.443 | -3.502%
| PL | 266.4 | 9.7227 | 56.1 | 62.8611 | -12.05%
| NL | 266.4 | 89.396 | 266.4 | 284.5857 | -6.826%
| PL | 309.7 | 10 | 65.2 | 69.4522 | -6.522%
| NL | 309.7 | 92.1726 | 309.7 | 298.1323 | 3.735%
| k1 | k2 | k3
| 2.7829 | 0.1344 | -3.6326
| 2.7829 | 0.1344 | -3.6326
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_EE_input | 1_Cooling |  |  | 2_EE_input | 2_Cooling
| 0.2 | 0.69098 |  |  | 1 | 2.9173

## Check Trane_A_Comp_Chill M
Model 96 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
96.2 | 2.91 | 33.0584
70.9 | 3.83 | 18.5117
45.6 | 5.33 | 8.5553
20.3 | 5.94 | 3.4175
Model 137 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
137 | 3.15 | 43.4921
101 | 4.22 | 23.9336
64.9 | 5.51 | 11.7786
28.9 | 6.28 | 4.6019
Model 236.7 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
236.7 | 3.14 | 75.3822
174.4 | 3.93 | 44.3766
112.1 | 5.23 | 21.434
49.8 | 6.01 | 8.2862
Model 309 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
309.7 | 3.36 | 92.1726
228.2 | 4.21 | 54.2043
146.7 | 5.71 | 25.6918
65.2 | 6.52 | 10

## Trane_A_COMPRESSION_Big
| Compression Chiller (air) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| Compression chiller large PL | 70.2 | 5.76 | [177] | 12.1875 | PL
| Compression chiller large NL | 334.2 | 3.27 | [177] | 102.2018 | NL
| Compression chiller large PL | 81.4 | 5.68 | [177] | 14.331 | PL
| Compression chiller large NL | 387.5 | 3.28 | [177] | 118.1402 | NL
| Compression chiller large PL | 96.1 | 5.73 | [177] | 16.7714 | PL
| Compression chiller large NL | 458 | 3.27 | [177] | 140.0612 | NL
| Compression chiller large PL | 113.4 | 5.39 | [177] | 21.039 | PL
| Compression chiller large NL | 540 | 3.35 | [177] | 161.194 | NL
| Compression chiller large PL | 122.5 | 5.44 | [177] | 22.5184 | PL
| Compression chiller large NL | 583 | 3.36 | [177] | 173.5119 | NL
| Compression chiller large PL | 133.7 | 5.32 | [177] | 25.1316 | PL
| Compression chiller large NL | 636.7 | 3.3 | [177] | 192.9394 | NL
| Compression chiller large PL | 145.3 | 5.65 | [177] | 25.7168 | PL
| Compression chiller large NL | 691.9 | 3.4 | [177] | 203.5 | NL
| Compression chiller large PL | 157.4 | 5.63 | [177] | 27.9574 | PL | 1_EE_input | 1_Cooling | 2_EE_input | 2_Cooling
| Compression chiller large NL | 750 | 3.35 | [177] | 223.8806 | NL | 27.9574 | 157.4 | 223.8806 | 750
| Compression chiller large PL | 173.9 | 5.73 | [177] | 30.349 | PL
| Compression chiller large NL | 828.2 | 3.32 | [177] | 249.4578 | NL
| Compression chiller large PL | 186.3 | 5.34 | [177] | 34.8876 | PL
| Compression chiller large NL | 887 | 3.28 | [177] | 270.4268 | NL
| Compression chiller large PL | 210.6 | 7.04 | [177] | 29.9148 | PL
| Compression chiller large NL | 1003 | 3.33 | [177] | 301.2012 | NL
| Compression chiller large PL | 235.4 | 7.1 | [177] | 33.1549 | PL
| Compression chiller large NL | 1121 | 3.3 | [177] | 339.697 | NL
| Compression chiller large PL | 263.8 | 6.9 | [177] | 38.2319 | PL
| Compression chiller large NL | 1254.6 | 3.32 | [177] | 377.8916 | NL
| Compression chiller large PL | 289.3 | 6.85 | [177] | 42.2336 | PL
| Compression chiller large NL | 1376 | 3.31 | [177] | 415.71 | NL
| Compression chiller large PL | 311.3 | 6.89 | [177] | 45.1814 | PL
| Compression chiller large NL | 1481 | 3.22 | [177] | 459.9379 | NL
| Compression chiller large PL | 339.8 | 7.07 | [177] | 48.0622 | PL
| Compression chiller large NL | 1616.9 | 3.15 | [177] | 513.3016 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  |  | Note: models RTAF HE LN R134a
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 334.2 | 12.1875 | 70.2 | 73.8064 | -5.137%
| NL | 334.2 | 102.2018 | 334.2 | 333.5219 | 0.2029%
| PL | 387.5 | 14.331 | 81.4 | 86.1538 | -5.84%
| NL | 387.5 | 118.1402 | 387.5 | 385.6713 | 0.4719%
| PL | 458 | 16.7714 | 96.1 | 101.3466 | -5.46%
| NL | 458 | 140.0612 | 458 | 457.0707 | 0.2029%
| PL | 540 | 21.039 | 113.4 | 123.1411 | -8.59%
| NL | 540 | 161.194 | 540 | 527.526 | 2.31%
| PL | 583 | 22.5184 | 122.5 | 132.3815 | -8.067%
| NL | 583 | 173.5119 | 583 | 568.0383 | 2.566%
| PL | 636.7 | 25.1316 | 133.7 | 146.1304 | -9.297%
| NL | 636.7 | 192.9394 | 636.7 | 630.3009 | 1.005%
| PL | 691.9 | 25.7168 | 145.3 | 154.2015 | -6.126%
| NL | 691.9 | 203.5 | 691.9 | 667.1537 | 3.577%
| PL | 750 | 27.9574 | 157.4 | 167.384 | -6.343%
| NL | 750 | 223.8806 | 750 | 732.675 | 2.31%
| PL | 828.2 | 30.349 | 173.9 | 183.3266 | -5.421%
| NL | 828.2 | 249.4578 | 828.2 | 815.5141 | 1.532%
| PL | 887 | 34.8876 | 186.3 | 203.2205 | -9.082%
| NL | 887 | 270.4268 | 887 | 882.8141 | 0.4719%
| PL | 1003 | 29.9148 | 210.6 | 202.285 | 3.948%
| NL | 1003 | 301.2012 | 1003 | 985.019 | 1.793%
| PL | 1121 | 33.1549 | 235.4 | 225.2776 | 4.3%
| NL | 1121 | 339.697 | 1121 | 1109.7335 | 1.005%
| PL | 1254.6 | 38.2319 | 263.8 | 255.3736 | 3.194%
| NL | 1254.6 | 377.8916 | 1254.6 | 1235.3828 | 1.532%
| PL | 1376 | 42.2336 | 289.3 | 280.9566 | 2.884%
| NL | 1376 | 415.71 | 1376 | 1358.536 | 1.269%
| PL | 1481 | 45.1814 | 311.3 | 301.6026 | 3.115%
| NL | 1481 | 459.9379 | 1481 | 1498.2861 | -1.167%
| PL | 1616.9 | 48.0622 | 339.8 | 325.6281 | 4.171%
| NL | 1616.9 | 513.3016 | 1616.9 | 1667.9683 | -3.158%
| k1 | k2 | k3
| 2.8853 | 0.11563 | 1.9366
| 2.8853 | 0.11563 | 1.9366
| L_min | 20%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_Heat_input | 1_Heat |  |  | 2_Heat_input | 2_Heat
| 0.2 | 0.69268 |  |  | 1 | 3.0009

## Check Trane_A_Comp_Chill B
Model 334 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
334.2 | 3.27 | 102.2018
248.1 | 3.85 | 64.4416
157.2 | 4.42 | 35.5656
70.2 | 5.76 | 12.1875
Model 828 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
828.2 | 3.32 | 249.4578
615.2 | 4.16 | 147.8846
389.5 | 4.6 | 84.6739
173.9 | 5.73 | 30.349
Model 1617 kW_th
Output [kw_th] | eff (EER) | input [kW_el]
1616.9 | 3.15 | 513.3016
1201.8 | 4.03 | 298.2134
760.5 | 5.31 | 143.2203
339.8 | 7.07 | 48.0622

## ALKALINE electrolyzer v2
| Alkaline Electrolyzer | Size_OUT [kw] | SEC [kw_Nm3] | eff (%) | ref eff, min load | input [kW_LHV]
| Alkaline Electrolyzer PL | 12.6662 | 5.9173 | 50.66% | [169] [171] | 25 | PL
| Alkaline Electrolyzer NL | 33.3111 | 4.5 | 66.62% | [169] | 50 | NL
| Alkaline Electrolyzer PL | 25.3324 | 5.9173 | 50.66% | [169] [171] | 50 | PL
| Alkaline Electrolyzer NL | 66.6222 | 4.5 | 66.62% | [169] | 100 | NL
| Alkaline Electrolyzer PL | 126.662 | 5.9173 | 50.66% | [169] [171] | 250 | PL
| Alkaline Electrolyzer NL | 333.1111 | 4.5 | 66.62% | [169] | 500 | NL
| Alkaline Electrolyzer PL | 253.324 | 5.9173 | 50.66% | [169] [171] | 500 | PL
| Alkaline Electrolyzer NL | 666.2222 | 4.5 | 66.62% | [169] | 1000 | NL
| Alkaline Electrolyzer PL | 506.648 | 5.9173 | 50.66% | [169] [171] | 1000 | PL
| Alkaline Electrolyzer NL | 1332.4444 | 4.5 | 66.62% | [169] | 2000 | NL
| Alkaline Electrolyzer PL | 1013.2961 | 5.9173 | 50.66% | [169] [171] | 2000 | PL
| Alkaline Electrolyzer NL | 2664.8889 | 4.5 | 66.62% | [169] | 4000 | NL
| Alkaline Electrolyzer PL | 2651.0653 | 5.6543 | 53.02% | [170][171] | 5000 | PL
| Alkaline Electrolyzer NL | 6972.093 | 4.3 | 69.72% | [170] | 10000 | NL
| Alkaline Electrolyzer PL | 5302.1306 | 5.6543 | 53.02% | [170][171] | 10000 | PL
| Alkaline Electrolyzer NL | 13944.186 | 4.3 | 69.72% | [170] | 20000 | NL
| Ref | Link
[169] | Mclyzer | https://cellar-c2.services.clever-cloud.com/com-mcphy/uploads/2020/08/20.05.McPhy_Portfolio_ELY_McLyzer_EN.pdf
[170] | Hydrogen from large-scale electrolysis | https://ucpcdn.thyssenkrupp.com/_binary/UCPthyssenkruppBAISUhdeChlorineEngineers/en/products/water-electrolysis-hydrogen-production/alkaline-water-electrolysis/link-thyssenkrupp_Hydrogen_Water_Electrolysis_and_green_chemicals.pdf
[171] | Highlights of alkaline electrolyzer development | https://www.finh2.fi/wp-content/uploads/highlights-of-alkaline-electrolyzer-development.pdf
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 33.3111 | 25 | 12.6662 | 13.7087 | -8.231%
| NL | 33.3111 | 50 | 33.3111 | 35.2649 | -5.865%
| PL | 66.6222 | 50 | 25.3324 | 27.4174 | -8.231%
| NL | 66.6222 | 100 | 66.6222 | 70.5298 | -5.865%
| PL | 333.1111 | 250 | 126.662 | 137.0869 | -8.231%
| NL | 333.1111 | 500 | 333.1111 | 352.6491 | -5.865%
| PL | 666.2222 | 500 | 253.324 | 274.1739 | -8.231%
| NL | 666.2222 | 1000 | 666.2222 | 705.2983 | -5.865%
| PL | 1332.4444 | 1000 | 506.648 | 548.3477 | -8.231%
| NL | 1332.4444 | 2000 | 1332.4444 | 1410.5965 | -5.865%
| PL | 2664.8889 | 2000 | 1013.2961 | 1096.6955 | -8.231%
| NL | 2664.8889 | 4000 | 2664.8889 | 2821.193 | -5.865%
| PL | 6972.093 | 5000 | 2651.0653 | 2668.7385 | -0.6666%
| NL | 6972.093 | 10000 | 6972.093 | 6979.9823 | -0.1132%
| PL | 13944.186 | 10000 | 5302.1306 | 5337.477 | -0.6666%
| NL | 13944.186 | 20000 | 13944.186 | 13959.9646 | -0.1132%
| k1 | k2 | k3
| 0.86225 | -0.23558 | -33.445
| 0.86225 | -0.23558 | -33.445
| L_min | 38%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_Heat_input | 1_Heat |  |  | 2_Heat_input | 2_Heat
| 0.38 | 0.092072 |  |  | 1 | 0.62667

## Check ALK el
| PL | SEC [kWh/kg_H2] | SEC [kWh/Nm3] | SECp/SECn
Alkaline el PL | 50% | 83.5 | 7.5175 | 1.315
Alkaline el PL | 60% | 74.5 | 6.7072 | 1.1732
Alkaline el PL | 70% | 69.5 | 6.2571 | 1.0945
Alkaline el PL | 80% | 66.5 | 5.987 | 1.0472
Alkaline el PL | 90% | 64.5 | 5.8069 | 1.0157
Alkaline el NL | 100% | 63.5 | 5.7169 | 1
Model 20000 kW_th | PL | SECp/SECn | SEC [kWh/Nm3] | eff [%] (LHV) | Output [kW_th] | Input [kW_th]
Alkaline el PL | 50% | 1.315 | 5.6543 | 53.02% | 10000 | 18860.3426
Alkaline el PL | 60% | 1.1732 | 5.0449 | 59.43% | 12000 | 20192.9896
Alkaline el PL | 70% | 1.0945 | 4.7063 | 63.7% | 14000 | 21977.3812
Alkaline el PL | 80% | 1.0472 | 4.5031 | 66.58% | 16000 | 24032.8198
Alkaline el PL | 90% | 1.0157 | 4.3677 | 68.64% | 18000 | 26223.7817
Alkaline el NL | 100% | 1 | 4.3 | 69.72% | 20000 | 28685.7905
HP applicata: % of output power in PL = % of current

## PEM electrolyzer
| PEM electrolyzer | Size [kw] | SEC [kw_kg] | eff (%) | ref eff, min load | input [kW_LHV]
| PEM electrolyzer PL | 56.0818 | 59.3776 | 56.08% | [176] | 100 | PL
| PEM electrolyzer NL | 605.4545 | 55 | 60.55% | [172] | 1000 | NL
| PEM electrolyzer PL | 70.8754 | 58.7298 | 56.7% | [176] | 125 | PL
| PEM electrolyzer NL | 765.1654 | 54.4 | 61.21% | [172][173] | 1250 | NL
| PEM electrolyzer PL | 115.5243 | 57.6502 | 57.76% | [176] | 200 | PL
| PEM electrolyzer NL | 1247.191 | 53.4 | 62.36% | [172][174] | 2000 | NL
| PEM electrolyzer PL | 144.9483 | 57.4343 | 57.98% | [176] | 250 | PL
| PEM electrolyzer NL | 1564.8496 | 53.2 | 62.59% | [172][173] | 2500 | NL
| PEM electrolyzer PL | 296.5864 | 56.1388 | 59.32% | [176] | 500 | PL
| PEM electrolyzer NL | 3201.9231 | 52 | 64.04% | [172][175] | 5000 | NL
| PEM electrolyzer PL | 1209.6075 | 55.0592 | 60.48% | [176] | 2000 | PL
| PEM electrolyzer NL | 13058.8235 | 51 | 65.29% | [172] | 20000 | NL
| Ref | Link
[172] | PEM Electrolyzers HyLYZER® Series | https://www.accelerazero.com/sites/default/files/2023-03/Electrolyzer%20Technologies%20-%20Brochure%20-%20Accelera%20by%20Cummins%20-%2003%2003%202023_0.pdf?utm_campaign=newpower-accelera-tradeshows&utm_content=&utm_medium=qr-code
[173] | HyLYZER® 250/500 | https://www.accelerazero.com/sites/default/files/2025-11/Accelera_HyLYZER_250_500_spec_sheet_2025.pdf
[174] | HyLYZER® 400/500 | https://www.accelerazero.com/sites/default/files/2025-09/HyLYZER-500-spec-sheet-2025.pdf
[175] | HyLYZER® 1000 | https://www.accelerazero.com/sites/default/files/2025-09/HyLYZER-1000-spec-sheet-2025.pdf
[176] | Reliable & HighPerformance PEM Electrolyser for the UK | https://hydrogenindustryleaders.com/8-elogen-11-24.pdf
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 605.4545 | 100 | 56.0818 | 63.0765 | -12.47%
| NL | 605.4545 | 1000 | 605.4545 | 654.0604 | -8.028%
| PL | 765.1654 | 125 | 70.8754 | 78.81 | -11.2%
| NL | 765.1654 | 1250 | 765.1654 | 817.5398 | -6.845%
| PL | 1247.191 | 200 | 115.5243 | 125.998 | -9.066%
| NL | 1247.191 | 2000 | 1247.191 | 1307.9656 | -4.873%
| PL | 1564.8496 | 250 | 144.9483 | 157.4724 | -8.64%
| NL | 1564.8496 | 2500 | 1564.8496 | 1634.9319 | -4.479%
| PL | 3201.9231 | 500 | 296.5864 | 314.636 | -6.086%
| NL | 3201.9231 | 5000 | 3201.9231 | 3269.5551 | -2.112%
| PL | 13058.8235 | 2000 | 1209.6075 | 1257.4705 | -3.957%
| NL | 13058.8235 | 20000 | 13058.8235 | 13077.1469 | -0.1403%
| k1 | k2 | k3
| 0.65665 | -0.004275 | -35.136
| 0.65665 | -0.004275 | -35.136
| L_min | 10%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_Heat_input | 1_Heat |  |  | 2_Heat_input | 2_Heat
| 0.1 | 0.06139 |  |  | 1 | 0.65237

## Check PEM el
| PL | SEC [kWh/kg_H2] | SEC [kWh/Nm3] | SECp/SECn
Alkaline el PL | 10% | 58.7582 | 5.29 | 1.0796
Alkaline el PL | 20% | 52.8712 | 4.76 | 0.97143
Alkaline el PL | 30% | 51.4273 | 4.63 | 0.9449
Alkaline el PL | 40% | 51.2051 | 4.61 | 0.94082
Alkaline el PL | 50% | 51.4273 | 4.63 | 0.9449
Alkaline el PL | 60% | 51.8716 | 4.67 | 0.95306
Alkaline el PL | 70% | 52.427 | 4.72 | 0.96327
Alkaline el PL | 80% | 53.0934 | 4.78 | 0.97551
Alkaline el PL | 90% | 53.8709 | 4.85 | 0.9898
Alkaline el NL | 100% | 54.4263 | 4.9 | 1
Model 20000 kW_th | PL | SECp/SECn | SEC [kWh/Nm3] | eff [%] (LHV) | Output [kW_th] | Input [kW_th]
Alkaline el PL | 10% | 1.0796 | 4.6422 | 64.58% | 2000 | 3096.8945
Alkaline el PL | 20% | 0.97143 | 4.1771 | 71.77% | 4000 | 5573.2393
Alkaline el PL | 30% | 0.9449 | 4.0631 | 73.79% | 6000 | 8131.5435
Alkaline el PL | 40% | 0.94082 | 4.0455 | 74.11% | 8000 | 10795.224
Alkaline el PL | 50% | 0.9449 | 4.0631 | 73.79% | 10000 | 13552.5725
Alkaline el PL | 60% | 0.95306 | 4.0982 | 73.15% | 12000 | 16403.5888
Alkaline el PL | 70% | 0.96327 | 4.142 | 72.38% | 14000 | 19342.4188
Alkaline el PL | 80% | 0.97551 | 4.1947 | 71.47% | 16000 | 22386.6251
Alkaline el PL | 90% | 0.9898 | 4.2561 | 70.44% | 18000 | 25553.7705
Alkaline el NL | 100% | 1 | 4.3 | 69.72% | 20000 | 28685.7905

## Water-Water HP_Small
| Water-Water HP (and geo) | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_el]
| HP (wate-water) PL | 9.7 | 5.8 | [177] | 1.6724 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (wate-water) NL | 63 | 4.33 | [177][179] | 14.5497 | NL | 1.5928 | 9.2381 | 13.8568 | 60
| HP (wate-water) PL | 11.7 | 5.84 | [177] | 2.0034 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (wate-water) NL | 76 | 4.28 | [177][179] | 17.757 | NL | 2.1089 | 12.3158 | 18.6916 | 80
| HP (wate-water) PL | 12.7 | 5.9 | [177] | 2.1525 | PL
| HP (wate-water) NL | 83 | 4.38 | [177][179] | 18.9498 | NL
| HP (wate-water) PL | 15.4 | 5.89 | [177] | 2.6146 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (wate-water) NL | 100 | 4.42 | [177][179] | 22.6244 | NL | 2.6146 | 15.4 | 22.6244 | 100
| HP (wate-water) PL | 17.6 | 5.79 | [177] | 3.0397 | PL
| HP (wate-water) NL | 115 | 4.44 | [177][179] | 25.9009 | NL
| HP (wate-water) PL | 20.8 | 5.9 | [177] | 3.5254 | PL
| HP (wate-water) NL | 135 | 4.46 | [177][179] | 30.2691 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE efficiency, refrigerant R454b, CXFW model, Tj=7 °C.
[179] | City Advantage CXWF Water-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=221
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 63 | 1.6724 | 9.7 | 8.9014 | 8.233%
| NL | 63 | 14.5497 | 63 | 63.2557 | -0.4059%
| PL | 76 | 2.0034 | 11.7 | 11.1532 | 4.674%
| NL | 76 | 17.757 | 76 | 77.6484 | -2.169%
| PL | 83 | 2.1525 | 12.7 | 12.2427 | 3.6%
| NL | 83 | 18.9498 | 83 | 83.1431 | -0.1725%
| PL | 100 | 2.6146 | 15.4 | 15.3106 | 0.5807%
| NL | 100 | 22.6244 | 100 | 99.7712 | 0.2288%
| PL | 115 | 3.0397 | 17.6 | 18.091 | -2.79%
| NL | 115 | 25.9009 | 115 | 114.5871 | 0.359%
| PL | 135 | 3.5254 | 20.8 | 21.4558 | -3.153%
| NL | 135 | 30.2691 | 135 | 134.3396 | 0.4892%
| k1 | k2 | k3
| 4.221 | 0.065735 | -2.2991
| 4.221 | 0.065735 | -2.2991
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.69888 |  |  | 1 | 4.2867

## EER_Water-Water HP_Small
| Water-Water HP (and geo) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| HP (wate-water) PL | 11.1 | 8.96 | [177] | 1.2388 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 52.7 | 5.04 | [177][179] | 10.4563 | NL | 1.3681 | 12.2584 | 11.5476 | 58.2
| HP (wate-water) PL | 12.7 | 8.75 | [177] | 1.4514 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 60.4 | 4.92 | [177][179] | 12.2764 | NL | 1.6384 | 14.3359 | 13.8577 | 68.18
| HP (wate-water) PL | 14.7 | 8.83 | [177] | 1.6648 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 69.7 | 5.03 | [177][179] | 13.8569 | NL | 2.2457 | 19.8292 | 18.6918 | 94.02
| HP (wate-water) PL | 17.6 | 8.88 | [177] | 1.982 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 83.6 | 5.04 | [177][179] | 16.5873 | NL | 2.7034 | 24.0063 | 22.625 | 114.03
| HP (wate-water) PL | 19.8 | 8.14 | [177] | 2.4324 | PL
| HP (wate-water) NL | 94 | 5 | [177][179] | 18.8 | NL
| HP (wate-water) PL | 23.4 | 8.24 | [177] | 2.8398 | PL
| HP (wate-water) NL | 111.2 | 5.04 | [177][179] | 22.0635 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE efficiency, refrigerant R454b, CXFW model, Tj=20 °C.
[179] | City Advantage CXWF Water-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=221
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 52.7 | 1.2388 | 11.1 | 10.8405 | 2.338%
| NL | 52.7 | 10.4563 | 52.7 | 52.5427 | 0.2985%
| PL | 60.4 | 1.4514 | 12.7 | 12.5477 | 1.199%
| NL | 60.4 | 12.2764 | 60.4 | 61.5225 | -1.859%
| PL | 69.7 | 1.6648 | 14.7 | 14.4133 | 1.951%
| NL | 69.7 | 13.8569 | 69.7 | 69.5731 | 0.182%
| PL | 83.6 | 1.982 | 17.6 | 17.194 | 2.307%
| NL | 83.6 | 16.5873 | 83.6 | 83.2719 | 0.3925%
| PL | 94 | 2.4324 | 19.8 | 20.2387 | -2.216%
| NL | 94 | 18.8 | 94 | 94.2895 | -0.3079%
| PL | 111.2 | 2.8398 | 23.4 | 23.7468 | -1.482%
| NL | 111.2 | 22.0635 | 111.2 | 110.7194 | 0.4322%
| k1 | k2 | k3
| 4.5242 | 0.096807 | 0.13396
| 4.5242 | 0.096807 | 0.13396
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.77544 |  |  | 1 | 4.621

## Water-Water HP_Mid
| Water-Water HP (and geo) | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_el]
| HP (wate-water) PL | 24 | 5.88 | [177] | 4.0816 | PL
| HP (wate-water) NL | 156 | 4.54 | [177][179] | 34.3612 | NL
| HP (wate-water) PL | 25.4 | 5.84 | [177] | 4.3493 | PL
| HP (wate-water) NL | 165 | 4.53 | [177][179] | 36.4238 | NL
| HP (wate-water) PL | 28.3 | 6.03 | [177] | 4.6932 | PL
| HP (wate-water) NL | 184 | 4.48 | [177][179] | 41.0714 | NL
| HP (wate-water) PL | 28.5 | 5.75 | [177] | 4.9565 | PL
| HP (wate-water) NL | 185 | 4.44 | [177][179] | 41.6667 | NL
| HP (wate-water) PL | 33.4 | 5.87 | [177] | 5.6899 | PL
| HP (wate-water) NL | 217 | 4.42 | [177][179] | 49.095 | NL
| HP (wate-water) PL | 41.2 | 5.81 | [177] | 7.0912 | PL
| HP (wate-water) NL | 268 | 4.37 | [177][179] | 61.3272 | NL
| HP (wate-water) PL | 45.4 | 5.94 | [177] | 7.6431 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (wate-water) NL | 295 | 4.43 | [177][179] | 66.5914 | NL | 7.7726 | 46.1695 | 67.7201 | 300
| HP (wate-water) PL | 50.3 | 5.94 | [177] | 8.468 | PL
| HP (wate-water) NL | 327 | 4.49 | [177][179] | 72.8285 | NL
| HP (wate-water) PL | 56.3 | 5.88 | [177] | 9.5748 | PL
| HP (wate-water) NL | 366 | 4.46 | [177][179] | 82.0628 | NL
| HP (wate-water) PL | 67.4 | 5.82 | [177] | 11.5808 | PL
| HP (wate-water) NL | 438 | 4.3 | [177][179] | 101.8605 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE efficiency, refrigerant R454b, CXFW model, Tj=7 °C.
[179] | City Advantage CXWF Water-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=221
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 156 | 4.0816 | 24 | 25.9597 | -8.165%
| NL | 156 | 34.3612 | 156 | 153.726 | 1.458%
| PL | 165 | 4.3493 | 25.4 | 27.3524 | -7.687%
| NL | 165 | 36.4238 | 165 | 162.6925 | 1.398%
| PL | 184 | 4.6932 | 28.3 | 29.3592 | -3.743%
| NL | 184 | 41.0714 | 184 | 182.8589 | 0.6201%
| PL | 185 | 4.9565 | 28.5 | 30.4995 | -7.016%
| NL | 185 | 41.6667 | 185 | 185.3998 | -0.2161%
| PL | 217 | 5.6899 | 33.4 | 34.5302 | -3.384%
| NL | 217 | 49.095 | 217 | 217.6801 | -0.3134%
| PL | 268 | 7.0912 | 41.2 | 41.9346 | -1.783%
| NL | 268 | 61.3272 | 268 | 270.7861 | -1.04%
| PL | 295 | 7.6431 | 45.4 | 45.0529 | 0.7645%
| NL | 295 | 66.5914 | 295 | 293.7883 | 0.4107%
| PL | 327 | 8.468 | 50.3 | 49.4696 | 1.651%
| NL | 327 | 72.8285 | 327 | 321.0419 | 1.822%
| PL | 366 | 9.5748 | 56.3 | 55.2805 | 1.811%
| NL | 366 | 82.0628 | 366 | 361.1471 | 1.326%
| PL | 438 | 11.5808 | 67.4 | 65.8505 | 2.299%
| NL | 438 | 101.8605 | 438 | 446.7902 | -2.007%
| k1 | k2 | k3
| 4.2195 | 0.029248 | 4.1744
| 4.2195 | 0.029248 | 4.1744
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.66218 |  |  | 1 | 4.2488

## EER_Water-Water HP_Mid
| Water-Water HP (and geo) | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| HP (wate-water) PL | 27.4 | 8.71 | [177] | 3.1458 | PL
| HP (wate-water) NL | 129.8 | 5.17 | [177][179] | 25.1064 | NL
| HP (wate-water) PL | 30.1 | 8.62 | [177] | 3.4919 | PL
| HP (wate-water) NL | 143.1 | 5.11 | [177][179] | 28.0039 | NL
| HP (wate-water) PL | 32.8 | 8.12 | [177] | 4.0394 | PL
| HP (wate-water) NL | 155.8 | 5.01 | [177][179] | 31.0978 | NL
| HP (wate-water) PL | 33.3 | 7.9 | [177] | 4.2152 | PL
| HP (wate-water) NL | 158 | 5.04 | [177][179] | 31.3492 | NL
| HP (wate-water) PL | 39 | 7.56 | [177] | 5.1587 | PL
| HP (wate-water) NL | 185 | 4.96 | [177][179] | 37.2984 | NL
| HP (wate-water) PL | 45.7 | 7.62 | [177] | 5.9974 | PL
| HP (wate-water) NL | 217.2 | 4.87 | [177][179] | 44.5996 | NL
| HP (wate-water) PL | 52.7 | 7.83 | [177] | 6.7305 | PL
| HP (wate-water) NL | 250.4 | 4.93 | [177][179] | 50.7911 | NL
| HP (wate-water) PL | 58.5 | 8.01 | [177] | 7.3034 | PL
| HP (wate-water) NL | 277.7 | 5.04 | [177][179] | 55.0992 | NL
| HP (wate-water) PL | 63.7 | 7.82 | [177] | 8.1458 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 302.7 | 4.99 | [177][179] | 60.6613 | NL | 9.0936 | 71.1117 | 67.7194 | 337.92
| HP (wate-water) PL | 69.8 | 7.52 | [177] | 9.2819 | PL
| HP (wate-water) NL | 331.4 | 4.77 | [177][179] | 69.4759 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE efficiency, refrigerant R454b, CXFW model, Tj=7 °C.
[179] | City Advantage CXWF Water-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=221
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 129.8 | 3.1458 | 27.4 | 28.3516 | -3.473%
| NL | 129.8 | 25.1064 | 129.8 | 127.0611 | 2.11%
| PL | 143.1 | 3.4919 | 30.1 | 30.7874 | -2.284%
| NL | 143.1 | 28.0039 | 143.1 | 140.9653 | 1.492%
| PL | 155.8 | 4.0394 | 32.8 | 34.089 | -3.93%
| NL | 155.8 | 31.0978 | 155.8 | 155.7125 | 0.05618%
| PL | 158 | 4.2152 | 33.3 | 35.0247 | -5.179%
| NL | 158 | 31.3492 | 158 | 156.9881 | 0.6404%
| PL | 185 | 5.1587 | 39 | 41.0529 | -5.264%
| NL | 185 | 37.2984 | 185 | 185.5158 | -0.2788%
| PL | 217.2 | 5.9974 | 45.7 | 46.9537 | -2.743%
| NL | 217.2 | 44.5996 | 217.2 | 220.4649 | -1.503%
| PL | 250.4 | 6.7305 | 52.7 | 52.4465 | 0.4811%
| NL | 250.4 | 50.7911 | 250.4 | 250.4921 | -0.03678%
| PL | 277.7 | 7.3034 | 58.5 | 56.8283 | 2.858%
| NL | 277.7 | 55.0992 | 277.7 | 271.6634 | 2.174%
| PL | 302.7 | 8.1458 | 63.7 | 62.2694 | 2.246%
| NL | 302.7 | 60.6613 | 302.7 | 298.319 | 1.447%
| PL | 331.4 | 9.2819 | 69.8 | 69.2758 | 0.7511%
| NL | 331.4 | 69.4759 | 331.4 | 339.8387 | -2.546%
| k1 | k2 | k3
| 4.4949 | 0.066187 | 5.6205
| 4.4949 | 0.066187 | 5.6205
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.74041 |  |  | 1 | 4.561

## Check W-W HP Small-Mid
63 kW_th
PL [%] | COP | Output | Input
| 4.33 | 63 | 14.5497
| 4.98 | 34 | 6.8273
| 5.57 | 21.8 | 3.9138
| 5.8 | 9.7 | 1.6724
165 kW_th
PL [%] | COP | Output | Input
| 4.53 | 165 | 36.4238
| 5.2 | 88.8 | 17.0769
| 5.76 | 57.1 | 9.9132
| 5.84 | 25.4 | 4.3493
438 kW_th
PL [%] | COP | Output | Input
| 4.3 | 438 | 101.8605
| 4.85 | 235.8 | 48.6186
| 5.49 | 151.6 | 27.6138
| 5.82 | 67.4 | 11.5808

## Water-Water HP_Big
| Water-Water HP (and Geo) | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_el]
| HP (wate-water) PL | 68 | 6 | [177] | 11.3333 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (wate-water) NL | 443 | 4.49 | [177][178] | 98.6637 | NL | 12.7916 | 76.7494 | 111.3586 | 500
| HP (wate-water) PL | 78.5 | 6.2 | [177] | 12.6613 | PL
| HP (wate-water) NL | 511 | 4.57 | [177][178] | 111.8162 | NL
| HP (wate-water) PL | 86.8 | 6.34 | [177] | 13.6909 | PL
| HP (wate-water) NL | 565 | 4.66 | [177][178] | 121.2446 | NL
| HP (wate-water) PL | 94.5 | 6.37 | [177] | 14.8352 | PL
| HP (wate-water) NL | 615 | 4.67 | [177][178] | 131.6916 | NL
| HP (wate-water) PL | 102.9 | 6.69 | [177] | 15.3812 | PL
| HP (wate-water) NL | 670 | 4.73 | [177][178] | 141.649 | NL
| HP (wate-water) PL | 111.3 | 6.77 | [177] | 16.4402 | PL
| HP (wate-water) NL | 725 | 4.77 | [177][178] | 151.9916 | NL
| HP (wate-water) PL | 121.8 | 6.71 | [177] | 18.152 | PL
| HP (wate-water) NL | 793 | 4.8 | [177][178] | 165.2083 | NL
| HP (wate-water) PL | 131.6 | 6.87 | [177] | 19.1557 | PL
| HP (wate-water) NL | 857 | 4.83 | [177][178] | 177.4327 | NL
| HP (wate-water) PL | 150.8 | 6.22 | [177] | 24.2444 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (wate-water) NL | 981 | 4.6 | [177][178] | 213.2609 | NL | 24.7139 | 153.7207 | 217.3913 | 1000
| HP (wate-water) PL | 158.3 | 6.21 | [177] | 25.4911 | PL
| HP (wate-water) NL | 1030 | 4.58 | [177][178] | 224.8908 | NL
| HP (wate-water) PL | 167.9 | 6.02 | [177] | 27.8904 | PL
| HP (wate-water) NL | 1093 | 4.58 | [177][178] | 238.6463 | NL
| HP (wate-water) PL | 177.2 | 6.07 | [177] | 29.1928 | PL
| HP (wate-water) NL | 1153 | 4.6 | [177][178] | 250.6522 | NL
| HP (wate-water) PL | 194.2 | 6.13 | [177] | 31.6803 | PL
| HP (wate-water) NL | 1264 | 4.63 | [177][178] | 273.0022 | NL
| HP (wate-water) PL | 223.7 | 6.61 | [177] | 33.8427 | PL
| HP (wate-water) NL | 1455 | 4.59 | [177][178] | 316.9935 | NL
| HP (wate-water) PL | 242.9 | 6.68 | [177] | 36.3623 | PL
| HP (wate-water) NL | 1581 | 4.61 | [177][178] | 342.9501 | NL
| HP (wate-water) PL | 262.3 | 6.85 | [177] | 38.292 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (wate-water) NL | 1707 | 4.66 | [177][178] | 366.309 | NL | 1121.616 | 7683.0697 | 10729.6137 | 50000
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R134a, RTWF model, High Vi (volume ratio), Tj=7 °C.
[178] | XStream™ RTWF Water-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=224
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 443 | 11.3333 | 68 | 73.3717 | -7.9%
| NL | 443 | 98.6637 | 443 | 458.2121 | -3.434%
| PL | 511 | 12.6613 | 78.5 | 82.4097 | -4.98%
| NL | 511 | 111.8162 | 511 | 519.3575 | -1.636%
| PL | 565 | 13.6909 | 86.8 | 89.4768 | -3.084%
| NL | 565 | 121.2446 | 565 | 563.4362 | 0.2768%
| PL | 615 | 14.8352 | 94.5 | 96.8622 | -2.5%
| NL | 615 | 131.6916 | 615 | 611.8159 | 0.5177%
| PL | 670 | 15.3812 | 102.9 | 101.8453 | 1.025%
| NL | 670 | 141.649 | 670 | 658.2724 | 1.75%
| PL | 725 | 16.4402 | 111.3 | 109.089 | 1.987%
| NL | 725 | 151.9916 | 725 | 706.4262 | 2.562%
| PL | 793 | 18.152 | 121.8 | 119.8187 | 1.627%
| NL | 793 | 165.2083 | 793 | 767.8546 | 3.171%
| PL | 857 | 19.1557 | 131.6 | 127.2405 | 3.313%
| NL | 857 | 177.4327 | 857 | 824.7227 | 3.766%
| PL | 981 | 24.2444 | 150.8 | 155.4746 | -3.1%
| NL | 981 | 213.2609 | 981 | 988.4173 | -0.7561%
| PL | 1030 | 25.4911 | 158.3 | 163.2646 | -3.136%
| NL | 1030 | 224.8908 | 1030 | 1041.9631 | -1.161%
| PL | 1093 | 27.8904 | 167.9 | 176.7892 | -5.294%
| NL | 1093 | 238.6463 | 1093 | 1105.5314 | -1.147%
| PL | 1153 | 29.1928 | 177.2 | 185.3397 | -4.593%
| NL | 1153 | 250.6522 | 1153 | 1161.2492 | -0.7155%
| PL | 1264 | 31.6803 | 194.2 | 201.5022 | -3.76%
| NL | 1264 | 273.0022 | 1264 | 1264.9402 | -0.07438%
| PL | 1455 | 33.8427 | 223.7 | 219.9805 | 1.663%
| NL | 1455 | 316.9935 | 1455 | 1467.7467 | -0.8761%
| PL | 1581 | 36.3623 | 242.9 | 236.9874 | 2.434%
| NL | 1581 | 342.9501 | 1581 | 1588.034 | -0.4449%
| PL | 1707 | 38.292 | 262.3 | 251.3947 | 4.158%
| NL | 1707 | 366.309 | 1707 | 1696.8738 | 0.5932%
| k1 | k2 | k3
| 4.4067 | 0.046854 | 2.6724
| 4.4067 | 0.046854 | 2.6724
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.70786 |  |  | 1 | 4.4536

## EER_Water-Water HP_Big
| Water-Water HP (and Geo) | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_el]
| HP (wate-water) PL | 89 | 7.46 | [177] | 11.9303 | PL
| HP (wate-water) NL | 422 | 4.61 | [177][178] | 91.5401 | NL
| HP (wate-water) PL | 103 | 7.74 | [177] | 13.3075 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 489 | 4.78 | [177][178] | 102.3013 | NL | 14.4856 | 112.1183 | 111.3577 | 532.29
| HP (wate-water) PL | 114 | 7.68 | [177] | 14.8438 | PL
| HP (wate-water) NL | 541 | 4.82 | [177][178] | 112.2407 | NL
| HP (wate-water) PL | 123 | 7.66 | [177] | 16.0574 | PL
| HP (wate-water) NL | 588 | 4.82 | [177][178] | 121.9917 | NL
| HP (wate-water) PL | 134 | 7.99 | [177] | 16.771 | PL
| HP (wate-water) NL | 637 | 4.87 | [177][178] | 130.8008 | NL
| HP (wate-water) PL | 144 | 8 | [177] | 18 | PL
| HP (wate-water) NL | 686 | 4.89 | [177][178] | 140.2863 | NL
| HP (wate-water) PL | 158 | 7.97 | [177] | 19.8243 | PL
| HP (wate-water) NL | 752 | 4.93 | [177][178] | 152.5355 | NL
| HP (wate-water) PL | 171 | 8.15 | [177] | 20.9816 | PL
| HP (wate-water) NL | 815 | 4.98 | [177][178] | 163.6546 | NL
| HP (wate-water) PL | 196 | 7.04 | [177] | 27.8409 | PL
| HP (wate-water) NL | 936 | 4.77 | [177][178] | 196.2264 | NL
| HP (wate-water) PL | 206 | 7.05 | [177] | 29.2199 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 981 | 4.74 | [177][178] | 206.962 | NL | 30.6922 | 216.3798 | 217.3903 | 1030.43
| HP (wate-water) PL | 219 | 7.04 | [177] | 31.108 | PL
| HP (wate-water) NL | 1041 | 4.73 | [177][178] | 220.0846 | NL
| HP (wate-water) PL | 231 | 6.65 | [177] | 34.7368 | PL
| HP (wate-water) NL | 1098 | 4.77 | [177][178] | 230.1887 | NL
| HP (wate-water) PL | 254 | 6.62 | [177] | 38.3686 | PL
| HP (wate-water) NL | 1210 | 4.82 | [177][178] | 251.0373 | NL
| HP (wate-water) PL | 292 | 6.83 | [177] | 42.7526 | PL
| HP (wate-water) NL | 1390 | 4.76 | [177][178] | 292.0168 | NL
| HP (wate-water) PL | 317 | 6.63 | [177] | 47.813 | PL
| HP (wate-water) NL | 1508 | 4.79 | [177][178] | 314.8225 | NL
| HP (wate-water) PL | 342 | 7.03 | [177] | 48.6486 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (wate-water) NL | 1629 | 4.83 | [177][178] | 337.2671 | NL | 1547.6781 | 10880.1768 | 10729.6066 | 51824
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R134a, RTWF model, Tj=20 °C, High Vi (volume ratio).
[178] | XStream™ RTWF Water-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=224
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 422 | 11.9303 | 89 | 93.4589 | -5.01%
| NL | 422 | 91.5401 | 422 | 445.3634 | -5.536%
| PL | 489 | 13.3075 | 103 | 103.8797 | -0.8541%
| NL | 489 | 102.3013 | 489 | 497.2646 | -1.69%
| PL | 541 | 14.8438 | 114 | 114.0336 | -0.02945%
| NL | 541 | 112.2407 | 541 | 544.5634 | -0.6587%
| PL | 588 | 16.0574 | 123 | 122.4382 | 0.4568%
| NL | 588 | 121.9917 | 588 | 590.7062 | -0.4602%
| PL | 637 | 16.771 | 134 | 128.7612 | 3.91%
| NL | 637 | 130.8008 | 637 | 632.8148 | 0.657%
| PL | 686 | 18 | 144 | 137.363 | 4.609%
| NL | 686 | 140.2863 | 686 | 677.913 | 1.179%
| PL | 752 | 19.8243 | 158 | 149.6957 | 5.256%
| NL | 752 | 152.5355 | 752 | 736.3274 | 2.084%
| PL | 815 | 20.9816 | 171 | 158.8857 | 7.084%
| NL | 815 | 163.6546 | 815 | 789.5524 | 3.122%
| PL | 936 | 27.8409 | 196 | 197.0318 | -0.5264%
| NL | 936 | 196.2264 | 936 | 941.3572 | -0.5723%
| PL | 981 | 29.2199 | 206 | 206.0376 | -0.01825%
| NL | 981 | 206.962 | 981 | 991.7228 | -1.093%
| PL | 1041 | 31.108 | 219 | 218.2641 | 0.336%
| NL | 1041 | 220.0846 | 1041 | 1053.6096 | -1.211%
| PL | 1098 | 34.7368 | 231 | 237.9915 | -3.027%
| NL | 1098 | 230.1887 | 1098 | 1101.9599 | -0.3606%
| PL | 1210 | 38.3686 | 254 | 261.2885 | -2.87%
| NL | 1210 | 251.0373 | 1210 | 1201.362 | 0.7139%
| PL | 1390 | 42.7526 | 292 | 292.3086 | -0.1057%
| NL | 1390 | 292.0168 | 1390 | 1394.1474 | -0.2984%
| PL | 1508 | 47.813 | 317 | 322.3089 | -1.675%
| NL | 1508 | 314.8225 | 1508 | 1502.5886 | 0.3588%
| PL | 1629 | 48.6486 | 342 | 333.8284 | 2.389%
| NL | 1629 | 337.2671 | 1629 | 1609.6271 | 1.189%
| k1 | k2 | k3
| 4.4204 | 0.064674 | 13.4304
| 4.4204 | 0.064674 | 13.4304
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.72773 |  |  | 1 | 4.485

## Check W-W HP Big
443 kW_th
PL [%] | COP | Output | Input
| 4.49 | 443 | 98.6637
| 4.97 | 238.5 | 47.9879
| 5.5 | 152.5 | 27.7273
| 6 | 68 | 11.3333
981 kW_th
PL [%] | COP | Output | Input
| 4.6 | 981 | 213.2609
| 5.19 | 526.3 | 101.4066
| 5.81 | 340.1 | 58.537
| 6.22 | 150.8 | 24.2444
1707 kW_th
PL [%] | COP | Output | Input
| 4.66 | 1707 | 366.309
| 5.33 | 920.5 | 172.7017
| 5.97 | 578.9 | 96.9682
| 6.85 | 262.3 | 38.292

## Trane_Air-Water HP_Smal
| Air-Water HP | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 2.9 | 4.02 | [177] | 0.72139 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 6 | 3.35 | [177][187] | 1.791 | NL | 0.60116 | 2.4167 | 1.4925 | 5
| HP (air-water) PL | 4.8 | 3.93 | [177] | 1.2214 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 10 | 3.52 | [177][187] | 2.8409 | NL | 1.2214 | 4.8 | 2.8409 | 10
| HP (air-water) PL | 6.9 | 3.94 | [177] | 1.7513 | PL
| HP (air-water) NL | 14 | 3.44 | [177][187] | 4.0698 | NL
| HP (air-water) PL | 9.9 | 4.11 | [177] | 2.4088 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 21 | 3.47 | [177][187] | 6.0519 | NL | 2.2941 | 9.4286 | 5.7637 | 20
| HP (air-water) PL | 10.4 | 4.82 | [177] | 2.1577 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 26 | 3.59 | [177][187] | 7.2423 | NL | 2.4896 | 12 | 8.3565 | 30
| HP (air-water) PL | 14.1 | 4.75 | [177] | 2.9684 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 35 | 3.39 | [177][187] | 10.3245 | NL | 3.3925 | 16.1143 | 11.7994 | 40
| HP (air-water) PL | 19.4 | 5.09 | [177] | 3.8114 | PL
| HP (air-water) NL | 41 | 3.52 | [177][187] | 11.6477 | NL
| HP (air-water) PL | 19.6 | 5.12 | [177] | 3.8281 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 48 | 3.26 | [177][187] | 14.7239 | NL | 3.9876 | 20.4167 | 15.3374 | 50
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for refrigerant R290, LEAF model, Tj=7 °C, Hydronic Pump is not considered in the data (consistency).
[187] | Trane Leaf Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=2110
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 6 | 0.72139 | 2.9 | 3.0413 | -4.874%
| NL | 6 | 1.791 | 6 | 5.9906 | 0.1562%
| PL | 10 | 1.2214 | 4.8 | 5.1821 | -7.961%
| NL | 10 | 2.8409 | 10 | 9.6476 | 3.524%
| PL | 14 | 1.7513 | 6.9 | 7.4054 | -7.325%
| NL | 14 | 4.0698 | 14 | 13.7981 | 1.442%
| PL | 21 | 2.4088 | 9.9 | 10.5522 | -6.588%
| NL | 21 | 6.0519 | 21 | 20.5971 | 1.919%
| PL | 26 | 2.1577 | 10.4 | 10.8127 | -3.968%
| NL | 26 | 7.2423 | 26 | 24.8323 | 4.491%
| PL | 35 | 2.9684 | 14.1 | 14.7631 | -4.703%
| NL | 35 | 10.3245 | 35 | 35.0455 | -0.13%
| PL | 41 | 3.8114 | 19.4 | 18.2308 | 6.027%
| NL | 41 | 11.6477 | 41 | 39.8373 | 2.836%
| PL | 48 | 3.8281 | 19.6 | 19.6108 | -0.05508%
| NL | 48 | 14.7239 | 48 | 49.653 | -3.444%
| k1 | k2 | k3
| 2.7572 | 0.19056 | -0.091051
| 2.7572 | 0.19056 | -0.091051
| L_min | 40%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.4 | 1.2935 |  |  | 1 | 2.9478

## EER_Trane_Air-Water HP_Smal
| Air-Water HP | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 2.9 | 5.76 | [177] | 0.50347 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 6.5 | 2.66 | [177][187] | 2.4436 | NL | 0.30518 | 1.7578 | 1.4812 | 3.94
| HP (air-water) PL | 4.8 | 5.72 | [177] | 0.83916 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 11.2 | 2.8 | [177][187] | 4 | NL | 0.59565 | 3.4071 | 2.8393 | 7.95
| HP (air-water) PL | 7.5 | 6.05 | [177] | 1.2397 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 16.7 | 2.82 | [177][187] | 5.922 | NL | 1.2063 | 7.2979 | 5.7624 | 16.25
| HP (air-water) PL | 10.7 | 6.57 | [177] | 1.6286 | PL
| HP (air-water) NL | 23 | 2.83 | [177][187] | 8.1272 | NL
| HP (air-water) PL | 11.1 | 6.36 | [177] | 1.7453 | PL
| HP (air-water) NL | 27.8 | 2.94 | [177][187] | 9.4558 | NL
| HP (air-water) PL | 13.8 | 6.34 | [177] | 2.1767 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 32.2 | 2.76 | [177][187] | 11.6667 | NL | 1.5588 | 9.8829 | 8.3551 | 23.06
| HP (air-water) PL | 14.8 | 6.19 | [177] | 2.391 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 37.4 | 2.77 | [177][187] | 13.5018 | NL | 2.0892 | 12.9322 | 11.7978 | 32.68
| HP (air-water) PL | 20.2 | 6.56 | [177] | 3.0793 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 51.8 | 2.96 | [177][187] | 17.5 | NL | 3.4056 | 22.3409 | 19.3547 | 57.29
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for refrigerant R290, LEAF model, Tj=20 °C, Hydronic Pump is not considered in the data (consistency).
[187] | Trane Leaf Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=2110
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 6.5 | 0.50347 | 2.9 | 2.7728 | 4.386%
| NL | 6.5 | 2.4436 | 6.5 | 6.7969 | -4.567%
| PL | 11.2 | 0.83916 | 4.8 | 4.775 | 0.5212%
| NL | 11.2 | 4 | 11.2 | 11.3309 | -1.169%
| PL | 16.7 | 1.2397 | 7.5 | 7.1339 | 4.882%
| NL | 16.7 | 5.922 | 16.7 | 16.8456 | -0.8716%
| PL | 23 | 1.6286 | 10.7 | 9.6911 | 9.429%
| NL | 23 | 8.1272 | 23 | 23.1699 | -0.7388%
| PL | 27.8 | 1.7453 | 11.1 | 11.2668 | -1.502%
| NL | 27.8 | 9.4558 | 27.8 | 27.2592 | 1.945%
| PL | 32.2 | 2.1767 | 13.8 | 13.384 | 3.014%
| NL | 32.2 | 11.6667 | 32.2 | 33.0674 | -2.694%
| PL | 37.4 | 2.391 | 14.8 | 15.2734 | -3.198%
| NL | 37.4 | 13.5018 | 37.4 | 38.3186 | -2.456%
| PL | 51.8 | 3.0793 | 20.2 | 20.7021 | -2.486%
| NL | 51.8 | 17.5 | 51.8 | 50.6124 | 2.293%
| k1 | k2 | k3
| 2.0741 | 0.27785 | -0.077502
| 2.0741 | 0.27785 | -0.077502
| L_min | 40%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.4 | 1.1075 |  |  | 1 | 2.352

## Check A-W HP Small
Da Manuale tecnico Aermec 0280-0750
NRL0600 | Potenza termica [%} | Potenza assorbita% | PL [%] | Efficiency Correction Factor | COP
1° Gradino di Potenza | 23 | 20 | 25 | 1.15
2° Gradino di Potenza | 48 | 45 | 50 | 1.0667
3° Gradino di Potenza | 73 | 70 | 75 | 1.0429
4° Gradino di Potenza | 100 | 100 | 100 | 1
Applicato a modello 26 kW
14 kW_th | Potenza termica [%} | Potenza assorbita% | Efficiency Correction Factor | COP | COP reale
1° Gradino di Potenza | 23 | 20 | 1.15
2° Gradino di Potenza | 48 | 45 | 1.0667 | 3.6693 | 3.94
3° Gradino di Potenza | 73 | 70 | 1.0429 | 3.5874 | n.a.
4° Gradino di Potenza | 100 | 100 | 1 | 3.44 | 3.44
Poiché PL min per modello 14 kW_th è circa 50% PL, applichiamo il punto PL a 73%
14 kW_th
PL [%] | COP | Output | Input
circa 50% | 3.94 | 6.9 | 1.7513
73% | 3.587 | 10.22 | 2.8492
100% | 3.44 | 14 | 4.0698
26 kW_th
PL [%] | COP | Output | Input
40% | 4.82 | 10.4 | 2.1577
73% | 3.7444 | 18.98 | 5.0689
100% | 3.59 | 26 | 7.2423
6 kW_th
PL [%] | COP | Output | Input
circa 50% | 4.02 | 2.9 | 0.72139
73% | 3.494 | 4.38 | 1.2536
100% | 3.35 | 6 | 1.791

## Trane_Air-Water HP_Mid
| Air-Water HP | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 8.1 | 3.91 | [177] | 2.0716 | PL
| HP (air-water) NL | 52 | 3.06 | [177][181] | 16.9935 | NL
| HP (air-water) PL | 8.2 | 4.14 | [177] | 1.9807 | PL
| HP (air-water) NL | 53 | 3.08 | [177][181] | 17.2078 | NL
| HP (air-water) PL | 8.9 | 3.93 | [177] | 2.2646 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 58 | 3.1 | [177][181] | 18.7097 | NL | 2.3427 | 9.2069 | 19.3548 | 60
| HP (air-water) PL | 10.5 | 4.72 | [177] | 2.2246 | PL
| HP (air-water) NL | 68 | 3.14 | [177][181] | 21.6561 | NL
| HP (air-water) PL | 12.5 | 5 | [177] | 2.5 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 81 | 3.02 | [177][181] | 26.8212 | NL | 2.4691 | 12.3457 | 26.4901 | 80
| HP (air-water) PL | 12.9 | 4.49 | [177] | 2.8731 | PL
| HP (air-water) NL | 84 | 3.11 | [177][181] | 27.0096 | NL
| HP (air-water) PL | 13.3 | 4.42 | [177] | 3.009 | PL
| HP (air-water) NL | 87 | 3.09 | [177][181] | 28.1553 | NL
| HP (air-water) PL | 16.4 | 4.6 | [177] | 3.5652 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 106 | 2.95 | [177][181] | 35.9322 | NL | 3.3634 | 15.4717 | 33.8983 | 100
| HP (air-water) PL | 16.8 | 4.64 | [177] | 3.6207 | PL
| HP (air-water) NL | 109 | 3.01 | [177][181] | 36.2126 | NL
| HP (air-water) PL | 18.5 | 4.63 | [177] | 3.9957 | PL
| HP (air-water) NL | 120 | 3.01 | [177][181] | 39.8671 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R454b, CXAX model, Tj=7 °C, LN (low noise), fans EC, Hydronic Pump is not considered in the data (consistency).
[181] | Conquest CXAX Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=215
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 52 | 2.0716 | 8.1 | 9.3722 | -15.71%
| NL | 52 | 16.9935 | 52 | 52.0579 | -0.1113%
| PL | 53 | 1.9807 | 8.2 | 9.1566 | -11.67%
| NL | 53 | 17.2078 | 53 | 52.7155 | 0.5368%
| PL | 58 | 2.2646 | 8.9 | 10.1913 | -14.51%
| NL | 58 | 18.7097 | 58 | 57.2343 | 1.32%
| PL | 68 | 2.2246 | 10.5 | 10.5217 | -0.2063%
| NL | 68 | 21.6561 | 68 | 66.1076 | 2.783%
| PL | 81 | 2.5 | 12.5 | 11.888 | 4.896%
| NL | 81 | 26.8212 | 81 | 81.4615 | -0.5698%
| PL | 84 | 2.8731 | 12.9 | 13.0886 | -1.462%
| NL | 84 | 27.0096 | 84 | 82.1341 | 2.221%
| PL | 87 | 3.009 | 13.3 | 13.6111 | -2.339%
| NL | 87 | 28.1553 | 87 | 85.545 | 1.672%
| PL | 106 | 3.5652 | 16.4 | 16.0475 | 2.15%
| NL | 106 | 35.9322 | 106 | 108.637 | -2.488%
| PL | 109 | 3.6207 | 16.8 | 16.3396 | 2.74%
| NL | 109 | 36.2126 | 109 | 109.5726 | -0.5254%
| PL | 120 | 3.9957 | 18.5 | 17.9018 | 3.234%
| NL | 120 | 39.8671 | 120 | 120.5161 | -0.4301%
| k1 | k2 | k3
| 2.8606 | 0.044493 | 1.1325
| 2.8606 | 0.044493 | 1.1325
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.47359 |  |  | 1 | 2.9051

## EER_Trane_Air-Water HP_Mid
| Air-Water HP | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 11.5 | 4.88 | [177] | 2.3566 | PL
| HP (air-water) NL | 54.9 | 3.04 | [177][181] | 18.0592 | NL
| HP (air-water) PL | 12.9 | 5.11 | [177] | 2.5245 | PL
| HP (air-water) NL | 61.4 | 2.96 | [177][181] | 20.7432 | NL
| HP (air-water) PL | 14.3 | 4.75 | [177] | 3.0105 | PL
| HP (air-water) NL | 67.7 | 2.84 | [177][181] | 23.838 | NL
| HP (air-water) PL | 15.7 | 4.65 | [177] | 3.3763 | PL
| HP (air-water) NL | 74.5 | 2.81 | [177][181] | 26.5125 | NL
| HP (air-water) PL | 18.8 | 6.09 | [177] | 3.087 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 89.2 | 2.92 | [177][181] | 30.5479 | NL | 2.6769 | 16.3025 | 26.4897 | 77.35
| HP (air-water) PL | 19.4 | 6.07 | [177] | 3.196 | PL
| HP (air-water) NL | 92.1 | 2.88 | [177][181] | 31.9792 | NL
| HP (air-water) PL | 21.5 | 5.67 | [177] | 3.7919 | PL
| HP (air-water) NL | 102.1 | 2.98 | [177][181] | 34.2617 | NL
| HP (air-water) PL | 22.8 | 5.47 | [177] | 4.1682 | PL
| HP (air-water) NL | 108.3 | 3.04 | [177][181] | 35.625 | NL
| HP (air-water) PL | 23.4 | 5.43 | [177] | 4.3094 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 111 | 2.85 | [177][181] | 38.9474 | NL | 3.7507 | 20.3664 | 33.8982 | 96.61
| HP (air-water) PL | 25.5 | 5.58 | [177] | 4.5699 | PL
| HP (air-water) NL | 121.2 | 2.92 | [177][181] | 41.5068 | NL
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R454b, CXAX model, Tj=7 °C, LN (low noise), fans EC, Hydronic Pump is not considered in the data (consistency).
[181] | Conquest CXAX Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=215
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 54.9 | 2.3566 | 11.5 | 11.2686 | 2.012%
| NL | 54.9 | 18.0592 | 54.9 | 52.3175 | 4.704%
| PL | 61.4 | 2.5245 | 12.9 | 12.6236 | 2.142%
| NL | 61.4 | 20.7432 | 61.4 | 60.2499 | 1.873%
| PL | 67.7 | 3.0105 | 14.3 | 14.7821 | -3.372%
| NL | 67.7 | 23.838 | 67.7 | 69.228 | -2.257%
| PL | 74.5 | 3.3763 | 15.7 | 16.6968 | -6.349%
| NL | 74.5 | 26.5125 | 74.5 | 77.1776 | -3.594%
| PL | 89.2 | 3.087 | 18.8 | 18.0121 | 4.191%
| NL | 89.2 | 30.5479 | 89.2 | 89.7986 | -0.6711%
| PL | 92.1 | 3.196 | 19.4 | 18.7058 | 3.578%
| NL | 92.1 | 31.9792 | 92.1 | 93.9487 | -2.007%
| PL | 102.1 | 3.7919 | 21.5 | 21.6727 | -0.8034%
| NL | 102.1 | 34.2617 | 102.1 | 101.325 | 0.7591%
| PL | 108.3 | 4.1682 | 22.8 | 23.5302 | -3.203%
| NL | 108.3 | 35.625 | 108.3 | 105.7625 | 2.343%
| PL | 111 | 4.3094 | 23.4 | 24.2799 | -3.76%
| NL | 111 | 38.9474 | 111 | 114.8281 | -3.449%
| PL | 121.2 | 4.5699 | 25.5 | 26.3983 | -3.523%
| NL | 121.2 | 41.5068 | 121.2 | 122.9565 | -1.449%
| k1 | k2 | k3
| 2.6141 | 0.14093 | -2.6288
| 2.6141 | 0.14093 | -2.6288
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.53305 |  |  | 1 | 2.7551

## Check A-W HP Mid
Da Manuale tecnico Aermec 0280-0750
NRL0600 | Potenza termica [%} | Potenza assorbita% | PL [%] | Efficiency Correction Factor | COP
1° Gradino di Potenza | 23 | 20 | 25 | 1.15
2° Gradino di Potenza | 48 | 45 | 50 | 1.0667
3° Gradino di Potenza | 73 | 70 | 75 | 1.0429
4° Gradino di Potenza | 100 | 100 | 100 | 1
Poiché PL min per modello 30 kW_th è circa 30% PL, applichiamo il punto PL a 73% e 48%
52 kW_th
PL [%] | COP | Output | Input
| 3.91 | 10.4 | 2.6598
48% | 3.4039 | 14.4 | 4.2305
73% | 3.1911 | 21.9 | 6.8627
100% | 3.06 | 30 | 9.8039
Poiché PL min per modello 68 kW_th è circa 35% PL, applichiamo il punto PL a 73% e 48%
68 kW_th
PL [%] | COP | Output | Input
| 4.57 | 23.7 | 5.186
48% | 3.4158 | 32.64 | 9.5555
73% | 3.275 | 49.64 | 15.1572
100% | 3.14 | 68 | 21.6561
Poiché PL min per modello 120 kW_th è circa 35% PL, applichiamo il punto PL a 73% e 48%
120 kW_th
PL [%] | COP | Output | Input
| 4.48 | 41.6 | 9.2857
48% | 3.2744 | 57.6 | 17.5909
73% | 3.1394 | 87.6 | 27.9032
100% | 3.01 | 120 | 39.8671

## Check A-W HP Mid v2
52 kW_th
PL [%] | COP | Output | Input
| 3.06 | 52 | 16.9935
| 3.31 | 28.2 | 8.5196
| 4.11 | 18.1 | 4.4039
| 3.91 | 8.1 | 2.0716
68 kW_th
PL [%] | COP | Output | Input
| 3.14 | 68 | 21.6561
| 3.46 | 36.8 | 10.6358
| 4.57 | 23.7 | 5.186
| 4.72 | 10.5 | 2.2246
120 kW_th
PL [%] | COP | Output | Input
| 3.01 | 120 | 39.8671
| 3.37 | 64.7 | 19.1988
| 4.48 | 41.6 | 9.2857
| 4.63 | 18.5 | 3.9957

## Trane_Air-Water HP_Big
| Air-Water HP | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 19.1 | 4.54 | [177] | 4.207 | PL
| HP (air-water) NL | 124 | 3.08 | [177][180] | 40.2597 | NL
| HP (air-water) PL | 24.1 | 4.94 | [177] | 4.8785 | PL
| HP (air-water) NL | 157 | 3.12 | [177][180] | 50.3205 | NL
| HP (air-water) PL | 26.2 | 4.76 | [177] | 5.5042 | PL
| HP (air-water) NL | 170 | 3.1 | [177][180] | 54.8387 | NL
| HP (air-water) PL | 29.6 | 4.35 | [177] | 6.8046 | PL
| HP (air-water) NL | 193 | 3.31 | [177][180] | 58.3082 | NL
| HP (air-water) PL | 30.2 | 4.76 | [177] | 6.3445 | PL
| HP (air-water) NL | 196 | 3.31 | [177][180] | 59.2145 | NL
| HP (air-water) PL | 34.8 | 4.99 | [177] | 6.9739 | PL
| HP (air-water) NL | 226 | 3.21 | [177][180] | 70.405 | NL
| HP (air-water) PL | 37.5 | 4.52 | [177] | 8.2965 | PL
| HP (air-water) NL | 244 | 3.37 | [177][180] | 72.4036 | NL
| HP (air-water) PL | 40.2 | 4.62 | [177] | 8.7013 | PL
| HP (air-water) NL | 261 | 3.31 | [177][180] | 78.852 | NL
| HP (air-water) PL | 44.1 | 4.66 | [177] | 9.4635 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 287 | 3.27 | [177][180] | 87.7676 | NL | 9.8922 | 46.0976 | 91.7431 | 300
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R454b, CXAF model, Tj=20°C, LN (low noise), Hydronic Pump is not considered in the data (consistency).
[180] | Sintesis Advantage CXAF Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=216
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 124 | 4.207 | 19.1 | 16.1423 | 15.49%
| NL | 124 | 40.2597 | 124 | 127.4305 | -2.767%
| PL | 157 | 4.8785 | 24.1 | 21.1361 | 12.3%
| NL | 157 | 50.3205 | 157 | 161.4073 | -2.807%
| PL | 170 | 5.5042 | 26.2 | 24.2181 | 7.565%
| NL | 170 | 54.8387 | 170 | 176.5049 | -3.826%
| PL | 193 | 6.8046 | 29.6 | 30.2681 | -2.257%
| NL | 193 | 58.3082 | 193 | 189.2503 | 1.943%
| PL | 196 | 6.3445 | 30.2 | 29.1135 | 3.598%
| NL | 196 | 59.2145 | 196 | 192.3136 | 1.881%
| PL | 226 | 6.9739 | 34.8 | 33.7118 | 3.127%
| NL | 226 | 70.405 | 226 | 229.5121 | -1.554%
| PL | 244 | 8.2965 | 37.5 | 39.3875 | -5.033%
| NL | 244 | 72.4036 | 244 | 237.2746 | 2.756%
| PL | 261 | 8.7013 | 40.2 | 42.1419 | -4.831%
| NL | 261 | 78.852 | 261 | 258.6845 | 0.8872%
| PL | 287 | 9.4635 | 44.1 | 46.7962 | -6.114%
| NL | 287 | 87.7676 | 287 | 288.5068 | -0.525%
| k1 | k2 | k3
| 3.0868 | 0.088516 | -7.8201
| 3.0868 | 0.088516 | -7.8201
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.55154 |  |  | 1 | 3.1753

## EER_Trane_Air-Water HP_Big
| Air-Water HP | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 26.9 | 6.19 | [177] | 4.3457 | PL
| HP (air-water) NL | 127.9 | 2.97 | [177][180] | 43.064 | NL
| HP (air-water) PL | 32.8 | 6.11 | [177] | 5.3682 | PL
| HP (air-water) NL | 155.7 | 3.09 | [177][180] | 50.3883 | NL
| HP (air-water) PL | 37.9 | 6.27 | [177] | 6.0447 | PL
| HP (air-water) NL | 180.1 | 2.95 | [177][180] | 61.0508 | NL
| HP (air-water) PL | 42.4 | 5.58 | [177] | 7.5986 | PL
| HP (air-water) NL | 201.1 | 2.78 | [177][180] | 72.3381 | NL
| HP (air-water) PL | 45.8 | 6.53 | [177] | 7.0138 | PL
| HP (air-water) NL | 217.8 | 3.16 | [177][180] | 68.9241 | NL
| HP (air-water) PL | 50.2 | 6.01 | [177] | 8.3527 | PL
| HP (air-water) NL | 238.3 | 3.1 | [177][180] | 76.871 | NL
| HP (air-water) PL | 55 | 6.09 | [177] | 9.0312 | PL
| HP (air-water) NL | 261.1 | 2.88 | [177][180] | 90.6597 | NL
| HP (air-water) PL | 55.6 | 6.09 | [177] | 9.1297 | PL
| HP (air-water) NL | 264.5 | 3.2 | [177][180] | 82.6562 | NL
| HP (air-water) PL | 60.8 | 6.19 | [177] | 9.8223 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 288.8 | 3.01 | [177][180] | 95.9468 | NL | 9.3938 | 58.1474 | 91.7608 | 276.2
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R454b, CXAF model, Tj=20°C, LN (low noise), Hydronic Pump is not considered in the data (consistency).
[180] | Sintesis Advantage CXAF Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=216
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 127.9 | 4.3457 | 26.9 | 25.8095 | 4.054%
| NL | 127.9 | 43.064 | 127.9 | 128.3339 | -0.3392%
| PL | 155.7 | 5.3682 | 32.8 | 32.2199 | 1.769%
| NL | 155.7 | 50.3883 | 155.7 | 151.4313 | 2.742%
| PL | 180.1 | 6.0447 | 37.9 | 37.2609 | 1.686%
| NL | 180.1 | 61.0508 | 180.1 | 182.9151 | -1.563%
| PL | 201.1 | 7.5986 | 42.4 | 44.1726 | -4.181%
| NL | 201.1 | 72.3381 | 201.1 | 215.6004 | -7.211%
| PL | 217.8 | 7.0138 | 45.8 | 44.8485 | 2.078%
| NL | 217.8 | 68.9241 | 217.8 | 208.7844 | 4.139%
| PL | 238.3 | 8.3527 | 50.2 | 51.1245 | -1.842%
| NL | 238.3 | 76.871 | 238.3 | 232.5579 | 2.41%
| PL | 261.1 | 9.0312 | 55 | 55.9578 | -1.741%
| NL | 261.1 | 90.6597 | 261.1 | 272.1068 | -4.216%
| PL | 264.5 | 9.1297 | 55.6 | 56.6715 | -1.927%
| NL | 264.5 | 82.6562 | 264.5 | 251.3668 | 4.965%
| PL | 288.8 | 9.8223 | 60.8 | 61.742 | -1.549%
| NL | 288.8 | 95.9468 | 288.8 | 289.7963 | -0.345%
| k1 | k2 | k3
| 2.648 | 0.13319 | -2.7332
| 2.648 | 0.13319 | -2.7332
| L_min | 15%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.15 | 0.53039 |  |  | 1 | 2.7812

## Check A-W HP Big-Huge
Da Manuale tecnico Aermec 0280-0750
NRL0600 | Potenza termica [%} | Potenza assorbita% | PL [%] | Efficiency Correction Factor | COP
1° Gradino di Potenza | 23 | 20 | 25 | 1.15
2° Gradino di Potenza | 48 | 45 | 50 | 1.0667
3° Gradino di Potenza | 73 | 70 | 75 | 1.0429
4° Gradino di Potenza | 100 | 100 | 100 | 1
Poiché PL min per modello 124 kW_th è circa 35% PL, applichiamo il punto PL a 73% e 48%
124 kW_th
PL [%] | COP | Output | Input
circa 30% | 4.55 | 43 | 9.4505
48% | 3.4261 | 59.52 | 17.3724
73% | 3.212 | 90.52 | 28.1818
100% | 3.08 | 124 | 40.2597
Poiché PL min per modello 261 kW_th è circa 35% PL, applichiamo il punto PL a 73% e 48%
261 kW_th
PL [%] | COP | Output | Input
circa 35% | 4.56 | 90.4 | 19.8246
48% | 3.6008 | 125.28 | 34.7925
73% | 3.4523 | 190.53 | 55.1888
100% | 3.31 | 261 | 78.852
Poiché PL min per modello 554 kW_th è circa 35% PL, applichiamo il punto PL a 73% e 48%
554 kW_th
PL [%] | COP | Output | Input
circa 35% | 4.95 | 191.7 | 38.7273
48% | 3.764 | 265.92 | 70.649
73% | 3.6088 | 404.42 | 112.0656
100% | 3.46 | 554 | 160.1156

## Check A-W HP Big v2
124 kW_th
PL [%] | COP | Output | Input
| 3.08 | 124 | 40.2597
| 3.41 | 66.9 | 19.6188
| 4.55 | 43 | 9.4505
| 4.54 | 19.1 | 4.207
196 kW_th
PL [%] | COP | Output | Input
| 3.31 | 196 | 59.2145
| 3.57 | 105.7 | 29.6078
| 4.71 | 67.9 | 14.4161
| 4.76 | 30.2 | 6.3445
287 kW_th
PL [%] | COP | Output | Input
| 3.27 | 287 | 87.7676
| 3.7 | 154.4 | 41.7297
| 4.68 | 99.3 | 21.2179
| 4.66 | 44.1 | 9.4635

## Trane_Air-Water HP_Huge
| Air-Water HP | Size [kw_th] | eff (COP) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 108.5 | 6.73 | [177] | 16.1218 | PL
| HP (air-water) NL | 335 | 3.49 | [177][180] | 95.9885 | NL
| HP (air-water) PL | 132.4 | 5.16 | [177] | 25.6589 | PL
| HP (air-water) NL | 356 | 3.47 | [177][180] | 102.5937 | NL
| HP (air-water) PL | 110.8 | 6.88 | [177] | 16.1047 | PL
| HP (air-water) NL | 392 | 3.4 | [177][180] | 115.2941 | NL
| HP (air-water) PL | 94.3 | 7.22 | [177] | 13.0609 | PL
| HP (air-water) NL | 409 | 3.48 | [177][180] | 117.5287 | NL
| HP (air-water) PL | 111.4 | 6.95 | [177] | 16.0288 | PL
| HP (air-water) NL | 423 | 3.48 | [177][180] | 121.5517 | NL
| HP (air-water) PL | 114.6 | 7.18 | [177] | 15.961 | PL
| HP (air-water) NL | 434 | 3.42 | [177][180] | 126.9006 | NL
| HP (air-water) PL | 141.2 | 7.16 | [177] | 19.7207 | PL | 1_EE_input | 1_Heat | 2_EE_input | 2_Heat
| HP (air-water) NL | 554 | 3.46 | [177][180] | 160.1156 | NL | 711.9376 | 5097.4729 | 5780.3468 | 20000
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R454b, CXAF model, Tj=7 °C, LN (low noise), fans EC, Hydronic Pump is not considered in the data (consistency).
[180] | Sintesis Advantage CXAF Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=216
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 335 | 16.1218 | 108.5 | 101.3018 | 6.634%
| NL | 335 | 95.9885 | 335 | 334.3394 | 0.1972%
| PL | 356 | 25.6589 | 132.4 | 131.9097 | 0.3703%
| NL | 356 | 102.5937 | 356 | 356.3924 | -0.1102%
| PL | 392 | 16.1047 | 110.8 | 108.7983 | 1.807%
| NL | 392 | 115.2941 | 392 | 398.2164 | -1.586%
| PL | 409 | 13.0609 | 94.3 | 102.168 | -8.344%
| NL | 409 | 117.5287 | 409 | 406.9874 | 0.4921%
| PL | 423 | 16.0288 | 111.4 | 112.6811 | -1.15%
| NL | 423 | 121.5517 | 423 | 420.5794 | 0.5723%
| PL | 434 | 15.961 | 114.6 | 113.9397 | 0.5761%
| NL | 434 | 126.9006 | 434 | 437.6428 | -0.8394%
| PL | 554 | 19.7207 | 141.2 | 140.7973 | 0.2852%
| NL | 554 | 160.1156 | 554 | 550.4462 | 0.6415%
| k1 | k2 | k3
| 2.9178 | 0.1324 | 9.9084
| 2.9178 | 0.1324 | 9.9084
| L_min | 25%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.25 | 0.86185 |  |  | 1 | 3.0502

## EER_Trane_Air-Water HP_Huge
| Air-Water HP | Size [kw_th] | eff (EER) | ref eff, min load | input [kW_el]
| HP (air-water) PL | 90.1 | 6.78 | [177] | 13.2891 | PL
| HP (air-water) NL | 299.5 | 3.25 | [177][180] | 92.1538 | NL
| HP (air-water) PL | 108.4 | 6.35 | [177] | 17.0709 | PL
| HP (air-water) NL | 330.5 | 3.14 | [177][180] | 105.2548 | NL
| HP (air-water) PL | 110.7 | 6.48 | [177] | 17.0833 | PL
| HP (air-water) NL | 372.8 | 3.08 | [177][180] | 121.039 | NL
| HP (air-water) PL | 137.7 | 6.13 | [177] | 22.4633 | PL
| HP (air-water) NL | 413.4 | 3.02 | [177][180] | 136.8874 | NL
| HP (air-water) PL | 95.6 | 7.21 | [177] | 13.2594 | PL
| HP (air-water) NL | 456.4 | 3.07 | [177][180] | 148.6645 | NL
| HP (air-water) PL | 114.1 | 6.82 | [177] | 16.7302 | PL
| HP (air-water) NL | 484.5 | 2.98 | [177][180] | 162.5839 | NL
| HP (air-water) PL | 115.6 | 6.9 | [177] | 16.7536 | PL
| HP (air-water) NL | 520.8 | 2.92 | [177][180] | 178.3562 | NL
| HP (air-water) PL | 117.9 | 7.22 | [177] | 16.3296 | PL | 1_EE_input | 1_Cool | 2_EE_input | 2_Cool
| HP (air-water) NL | 574.3 | 3.04 | [177][180] | 188.9145 | NL | 499.6421 | 3607.4156 | 5780.2632 | 17572
| Ref | Link
[177] | Ecodesign Datasheet Management | https://ecodesign.tranetechnologies.com/ords/r/stsbx/ecodesigndatasheetmgmt/home |  |  |  | NOTE: Data for HE (high efficiency), refrigerant R454b, CXAF model, Tj=20 °C, LN (low noise), fans EC, Hydronic Pump is not considered in the data (consistency).
[180] | Sintesis Advantage CXAF Air-to-Water Heat Pump | https://trane.eu/uk/equipment/product-details.html?prodId=216
|  |  |  | HEAT | HEAT | HEAT
| Point | XD (size) [kW_th] | In (input) [kW_LHV] | Out (output) [kW_th] | Out calc (output) [kW_th] | Out err
| PL | 299.5 | 13.2891 | 90.1 | 96.7359 | -7.365%
| NL | 299.5 | 92.1538 | 299.5 | 297.1527 | 0.7837%
| PL | 330.5 | 17.0709 | 108.4 | 107.751 | 0.5987%
| NL | 330.5 | 105.2548 | 330.5 | 331.8503 | -0.4086%
| PL | 372.8 | 17.0833 | 110.7 | 109.6992 | 0.9041%
| NL | 372.8 | 121.039 | 372.8 | 373.8787 | -0.2893%
| PL | 413.4 | 22.4633 | 137.7 | 125.2106 | 9.07%
| NL | 413.4 | 136.8874 | 413.4 | 415.9934 | -0.6273%
| PL | 456.4 | 13.2594 | 95.6 | 103.7691 | -8.545%
| NL | 456.4 | 148.6645 | 456.4 | 447.8704 | 1.869%
| PL | 484.5 | 16.7302 | 114.1 | 113.8626 | 0.208%
| NL | 484.5 | 162.5839 | 484.5 | 484.5165 | -0.0034%
| PL | 520.8 | 16.7536 | 115.6 | 115.5668 | 0.02872%
| NL | 520.8 | 178.3562 | 520.8 | 526.2428 | -1.045%
| PL | 574.3 | 16.3296 | 117.9 | 116.9133 | 0.8369%
| NL | 574.3 | 188.9145 | 574.3 | 555.4982 | 3.274%
| k1 | k2 | k3
| 2.5413 | 0.045307 | 49.3952
| 2.5413 | 0.045307 | 49.3952
| L_min | 25%
| L_Max | 100%
Point 1 corresponds to minimum load, point 2 to nominal/max load
| 1_NG | 1_Heat |  |  | 2_NG | 2_Heat
| 0.25 | 0.68063 |  |  | 1 | 2.5866

## Check A-W HP Huge v2
335 kW_th
PL [%] | COP | Output | Input
| 3.49 | 335 | 95.9885
| 3.85 | 180.2 | 46.8052
| 5.14 | 115.8 | 22.5292
| 6.73 | 108.5 | 16.1218
409 kW_th
PL [%] | COP | Output | Input
| 3.48 | 409 | 117.5287
| 3.82 | 220.2 | 57.644
| 4.81 | 141.5 | 29.4179
| 7.22 | 94.3 | 13.0609
554 kW_th
PL [%] | COP | Output | Input
| 3.46 | 554 | 160.1156
| 3.77 | 298.3 | 79.1247
| 4.95 | 191.7 | 38.7273
| 7.16 | 141.2 | 19.7207